## Input's from BD(Sales)
DOC. No: 4PEL/DES-SSR/109 #I01, R05.
|  | Issue Date: 23/02/2026. | [5 empty] | Client Scope | Client Scope | Ground | Cable Tray | Required | Domestic | Client Scope | Client Scope
|  | Control Copy No. 02. | [5 empty] | Trenching | Not Required | Roof | Client Scope | Not Required | Imported | Already Exist | 4PEL Scope
Site Surrvey Request Form | [7 empty] | Existing Trench | 4PEL Scope |  | Trenching |  |  | 4PEL Scope | Not Required
Site Visit Request Form (To be filled by Sales Team) |  | Remarks | Remarks |  |  |  |  | Cable Tray | [5 empty] | Not Required
Name of BD Person | Carl Aaron
Mobile No. | 9551062519
Mail id | carl.aaron@fourthpartner.co
Site visit Request date
State | Maharashtra
Client name | West Pioneer Properties
Mode of site survey | Physical
Location & address | Metro Junction Mall, Kalyan - Shilphata Rd, Kalyan East, Kalyan, Maharashtra 421306
Lat & Long details | 19°13'45.98"N 73°07'23.94"E
This Project having RFQ/RFP | Yes
Plant Type (Capex/Opex) | Capex
Expected Cap in Kwp | 400
No. of locations | 1
Type of installation | RCC
Module wattage (Wp) | 595 / 590 / 585
Module Origin | ALMM Approved
Prefered Inverter make | Solis / Sungrow / Equivalent
DC/AC Ratio
AMC & Module Cleaning |  | Capex Model
No. of Years of AMC & Module cleaning |  | Capex Model
PBG Amount % |  | Capex Model
No. of Yrs BG is required to be maintained |  | Capex Model
Marketing Commission % | 0% | 0 | /Wp
EPC Margin % | 10% | 3.5242 | /Wp
Scope of Work |  | Remarks
For Rooftop
Access to the Roof | Client Scope
Gutter for cleaning/ Rain Water Harvesting | Not Required
Scope of mesh over the skylight | Not Required
Scope of Turbo vent | Not Applicable
Hand Railling | 4PEL Scope
Walkways materials | FRP
DC Cable Tray materials | FRP
AC Cable Tray materials (INV And ACCB panel) | GI
AC Cable Tray materials (ACCB And CLT panel) | GI
Roof puncturing permission from client for :
Modules (MMS)
Walkway Dimension (w)
Lifeline location
Anchoring permission for RCC
PV Syst
For Ground mounted/ Parking
Soil Test (Ground /Parking)
Land Leveling (Ground /Parking)
Peripheral Plant Fencing
Type of Peripheral Plant Fencing
Peripheral Lighting
Plant Approach Road (Out side the Plant) (WBM Road)
Internal Road (WBM Type)
Peripheral Road (WBM type)
Strom Water Drainage
For Floating
Bathymetry test & CFD study
Common Factors for Rooftop & Ground mounted
Spare Feeder (Termination Feeder) | Client Scope
CEIG Liaisoning / Minister cost | 4PEL Scope
Netmeter Liaisoning & NOC | 4PEL Scope
Type of Netmetering | Net Metering/Net Billing
Netmeter material & installation for Discom | 4PEL Scope
Metering Cubicle (CT&PT) with Installtion | Client Scope
Renewable Purchase Obligation (RPO) | Client Scope
Generation Panel before client termination | 4PEL Scope
Control Room | Client Scope
Spare Material Requirement | Not Applicable
Inverter Ext. warranty Requirement if any? | No
Plant Extra Warranty for BOS | No
No. of Year's Plant Extra Warranty for BOS | 0
Site Contact Person Details
Contact Person at site | Mr. Anil Kumar
Mob No. | 9324592021
Land line no.
Mail id
Designation
Power bills | Collected
CEIG report (Approval Status)
Plant cad files | Available
Plant SLD cad file | Available
Mobile Access | Yes, Client allows mobile usage inside their premises
Roof Access | Yes, Roof access available
Preferring date (to be conf from survey coordinator)
Comments(if any):
Client Scope
4PEL Scope
Not Required
Already Exist
Not Applicable
Monkey
Staircase
Movable
Not Applicable
Required
Not Required
Not Applicable | Pre-Fab Wall | 3600
Avenue Supermarts Limited | Chain Link Mesh | 1600
ITC | Not Applicable | 0
Net Metering/Net Billing
Behind The Meter
| Formulas are there -------> | selection by project type |  | Formulas are there down
| Project type | Category | Options
| Capex | Walkways materials | GI | Walkways materials | GI
| Capex | Walkways materials | FRP |  | FRP
| Capex | Walkways materials | HDG |  | HDG
| Capex/Opex | Walkways materials | GI |  |  | FRP
| Capex/Opex | Walkways materials | FRP |  |  | HDG
| Capex/Opex | Walkways materials | HDG |  |  | Not Applicable
| Opex | Walkways materials | FRP
| Opex | Walkways materials | HDG
| Capex | DC Cable Tray materials | GI | DC Cable Tray materials | GI | FRP
| Capex | DC Cable Tray materials | FRP |  | FRP | HDG
| Capex | DC Cable Tray materials | HDG |  | HDG | Soil Trench
| Capex | DC Cable Tray materials | Soil Trench |  | Soil Trench | Not Applicable | [8 empty] | Client Scope | Client Scope | Ground | Cable Tray | Required | Domestic | Client Scope | Client Scope | Monkey
| Capex/Opex | DC Cable Tray materials | GI | [11 empty] | Trenching | Not Required | Roof | Client Scope | Not Required | Imported | Already Exist | 4PEL Scope | Staircase
| Capex/Opex | DC Cable Tray materials | FRP | [11 empty] | Existing Trench | 4PEL Scope |  | Trenching |  |  | 4PEL Scope | Not Required | Movable
| Capex/Opex | DC Cable Tray materials | HDG | [11 empty] | Cable Tray | [5 empty] | Not Required
| Capex/Opex | DC Cable Tray materials | Soil Trench | [11 empty] | Not Required
| Opex | DC Cable Tray materials | FRP
| Opex | DC Cable Tray materials | HDG
| Opex | DC Cable Tray materials | Soil Trench
| Capex | AC Cable Tray materials (INV And ACCB panel) | Not Applicable | AC Cable Tray materials (INV And ACCB panel) | Not Applicable
| Capex | AC Cable Tray materials (INV And ACCB panel) | GI |  | GI
| Capex | AC Cable Tray materials (INV And ACCB panel) | HDG |  | HDG
| Capex | AC Cable Tray materials (INV And ACCB panel) | POWDER COATED |  | POWDER COATED
| Capex | AC Cable Tray materials (INV And ACCB panel) | Soil Trench |  | Soil Trench
| Capex/Opex | AC Cable Tray materials (INV And ACCB panel) | Not Applicable
| Capex/Opex | AC Cable Tray materials (INV And ACCB panel) | GI
| Capex/Opex | AC Cable Tray materials (INV And ACCB panel) | HDG
| Capex/Opex | AC Cable Tray materials (INV And ACCB panel) | POWDER COATED
| Capex/Opex | AC Cable Tray materials (INV And ACCB panel) | Soil Trench
| Opex | AC Cable Tray materials (INV And ACCB panel) | Not Applicable
| Opex | AC Cable Tray materials (INV And ACCB panel) | HDG
| Opex | AC Cable Tray materials (INV And ACCB panel) | POWDER COATED
Along with Walkways | Opex | AC Cable Tray materials (INV And ACCB panel) | Soil Trench
As. Per 4PEL Std.
Not Applicable
Available
Not Available
Not Applicable
As. Per 4PEL Std.
No
YES
Not Applicable
Not Required
LT | bike/car/truck
HT | Bike |  |  |  | Inputs from BD for Pre-design |  | Site visit report
Car
Yes, Roof access available | Truck/Bus
No, Roof access is not available | Not Required
Client will arrange
Not Applicable
Collected
Not collected
Yes, Client allows mobile usage inside their premises
No,Client doesn’t allows mobile usage inside their premises
Client will arrange facility for taking photos in side the Premises.
300mm
No, As Per 4PEL Std | 400mm
Yes | 500mm
| 600mm | Capex | 970
| 1000mm | Opex | 1450
| Not Applicable | Capex/Opex | 970
Online
Physical
Yes, Client allows puncturing of roofing sheet.
No, Adhesive technology to be used
Others
Not Applicable
Yes, Client allows anchoring for RCC
No, Client dosen't allows anchoring for RCC
Others
Not Applicable
Domestic
Imported
Mono-crystalline
Poly-crystalline
String
States | map values | Column1 |  | distance
Andhra Pradesh | 0 |  | Andhra Pradesh | 700
Arunachal Pradesh | 0 |  | Arunachal Pradesh | 2800
Assam | 0 |  | Assam | 2500
Bihar | 0 |  | Jharkhand | 1500
Chhattisgarh | 0 |  | Karnataka | 900
Goa | 0 |  | Kerala | 700
Gujarat | 0 |  | Manipur | 1300
Haryana | 0 |  | Meghalaya | 1900
Himachal Pradesh | 0 |  | Mizoram | 2200
Jammu and Kashmir | 0 |  | Nagaland | 2200
Jharkhand | 0 |  | Odisha | 1450
Karnataka | 0 |  | Sikkim | 700
Kerala | 0 |  | Tamil Nadu | 1300
Madhya Pradesh | 0 |  | Telangana | 950
Maharashtra | 1 |  | West Bengal | 750
Manipur | 0 |  | Pondicherry | 2900
Meghalaya | 0 |  |  | 2450
Mizoram | 0 |  |  | 3000
Nagaland | 0 |  |  | 3000
Odisha | 0 |  |  | 1000
Punjab | 0 |  |  | 2100
Rajasthan | 0 |  |  | 1500
Sikkim | 0 |  |  | 3000
Tamil Nadu | 0 |  |  | 900
Telangana | 0 |  |  | 500
Tripura | 0 |  |  | 3000
Uttar Pradesh | 0 |  |  | 1600
Uttarakhand | 0 |  |  | 1900
West Bengal | 0 |  |  | 1550
Daman & Diu | 0 |  |  | 750
Pondicherry | 0 |  |  | 900
Dadra & Nagar Haveli | 0 |  |  | 900
Delhi | 0 |  |  | 1750
This chart isn't available in your version of Excel. Editing this shape or saving this workbook into a different file format will permanently break the chart.

## Consumption analysis (BD)
| Fourth Partner Energy Pvt. Ltd |  |  | DOC. No: 4PEL/DES-CA/555 #I01, R00.
Issue Date: 11/12/2023.
Control Copy No. 02.
Consumption Analysis
A) | E Bill Parameters
| 0 | [6 empty] | 277 |  | 277
| Months | Off Peak hrs (10 PM-05:30 AM) | Normal hrs 05:30 AM-05:30 PM) | Peak Hrs (TOU) (05:30 PM-10PM) | Total Monthly consumption from DISCOM | Generation at 277kWp |  | Energy Per kWp (kWh) | Capacity (kWP) as per day time consumption |  | Difference of Consumption vs Generation (kWH) | Banking Charges | Note - 1. TOD zone will differ as per state regulatories norms, State DISCOM's 2.Yield will differ as per location & type of installation, module type. 3. Actual proposed size is based on shadow free area on roof/ground , state regulatories norms
| May'24 |  |  |  |  | 30.74 | 28.6435 | 103.4063 | 0 | 28643.532 | -28643.532 | -42965.298
| April'24 |  |  |  |  | 34.39 | 32.0446 | 115.6845 | 0 | 32044.602 | -32044.602 | -48066.903
[6 empty] | 29.89 | 27.8515 | 100.5469 | 0 | 27851.502 | -27851.502 | -41777.253
| Total |  |  |  | 0 |  |  |  | 0
| Considering Day time consumption only |  |  | Considering Overall consumption |  |  |  |  | 0
| Monthly Min Consumption | #DIV/0! |  | Monthly Avg Consumption | #DIV/0! |  | Minimum Capacity (kWP) considering 12 months
| 70% of Avergae Consumption to avoid Banking charges | #DIV/0! |  | Min offtake Guarantee to Discom (If any) | 0 |  | *March , April'2020 not considered due to COVID
| Net consumption available for offset by Solar | #DIV/0! |  | Net consumption available for offset by Solar | #DIV/0!
| Daily Avg Consumption | #DIV/0! |  | Daily Avg Consumption | #DIV/0!
| Yield |  |  | Yield
| SPP Size based on consumption (kWp) | #DIV/0! |  | SPP Size based on consumption (kWp) | #DIV/0!
| Actual Proposed SPP size (kWp) |  |  |  | 0
| % day time consumption replaced |  | #DIV/0!
| % overall consumption replaced |  | #DIV/0!
B) | Operational Parameters
What is manufactured/Processed? Any heat / exhaust issues?
Describe the load pattern? Constant/Seasonal/Order based
Check the feasibility of obtaining 15 min load profile from client?
No. of days per week plant is operational
No. of shifts in which plant is operational
Age of facility
If ToD data not available, what is % day time consumption as per client input/experience
C) | Capacity assesment
| Parameters | Maximum Installed Capacity (kWp) | Remarks
| Based on G-Map | 0
Based on Consumption analysis
| Based on State regulatory norms (Net Metering or Min offtake commitment to Discom) | 0
| Proposed Capacity | 0
D) | Bill Analysis
| May'24 |  |  |  | Billing Month
| Sanctioned Load/CD- 4950KVA |  |  |  | March
| Particulars | Units | Rate | Amount
| Total Charges |  | #DIV/0!
| Less : Demand Charges/Fixed Charges |  | #DIV/0!
| Grid Variable cost/ Landed cost of power | 0 | #DIV/0! | 0
Breakup of LCOP
| Energy Cost | 0 | #DIV/0!
| Meter Rent | 0 | #DIV/0!
| ED | 0 | #DIV/0!
| Delayed Payment Surcharge | 0 | #DIV/0!
| IDF | 0 | #DIV/0!
| TCS Rate | 0 | #DIV/0!
| PF Incentive | 0 | #DIV/0!
| Customer Service Charge | 0 | #DIV/0!
| Incentive on TODs | 0 | #DIV/0!
| for check 1 |  |  | 0
0
E) | Savings
|  | Annual Energy Consumption (kWh) | Est Variable Grid Tariff (₹/kWh) | Proposed Rooftop Capacity (kWp) | Est Annual Solar Generation (kWh) | [7 empty] | % savngs in Variable Grid Tariff | Annual Savings Per Site (₹) | Overall Savings %
| Onsite | 0 | #DIV/0! | 0 | 0 | [7 empty] | #DIV/0! | #DIV/0! | #DIV/0!
Offsite

## ESG (Design)
| INITIAL SITE SURVEY – ESG CHECKLIST |  |  |  | DOC. No: 4PEL/DES-ISS/554 #I01, R00.
Issue Date: 11/12/2023.
Control Copy No.: 02.
Name of Project Site | Metro Junction mall
Location/Address | Metro Junction mall, Kalyan East |  | State |  | Maharashtra
Country | India
Name of Surveyor | Sagar Chavan |  | Date |  | 2026-05-11
Department of Surveyor | Design
Name of Verifier
Department of Verifier
Aspects to check |  | Yes | No | NA | Remarks
Key safety checks (evidence shall be provided against each significant check point with appropriate remark)
Is suitable instrument available for taking actual measurements? |  | yes
Is any other technology other than manual measurement being used? (Ex. Drone etc.) |  |  | No
Is proper roof access available for roof? |  | Yes
If yes, what type of access is available, Monkey ladder, Step ladder or other? (Provide details in remark)
If monkey ladder height is more than 10 meters, then is/are the rest platforms provided? |  |  |  | NA
(After every 10 meters there shall be minimum 10 meters gap between two platforms)
Is ladder extended 1 meter above the roof? |  |  |  | NA
Is/are skylight(s) available on the roof? |  |  |  | NA
(If yes, please mention quantity and dimensions of the skylight)
Is/are existing lifeline(s) available? |  |  |  | NA
If yes, please provide details. (Attach photographs)
If 2 or more roofs are interconnected, is safe access available for roof-to-roof access? |  |  |  | NA
Please provide the access details.
Is/are Turbo wind ventilator(s) available on roof? |  |  |  | NA
(If yes, please provide total numbers)
Is alternative access available for the roof? |  | Yes
Has client provided Wire mesh below/above skylights for fall protection? |  |  |  | NA
If yes, does all the skylights on the roof are being covered?
Is there any chemical / Hazardous waste emission on top of the roof? |  |  | No
Is there any Electric cables/ Pipes/Unprojected pipes routed on the roof? |  | Yes
Is lightning arrester available? If yes, does it cover all the roof area? |  | Yes |  |  | under exectuion, may not cover entire roof
Are guard rails provided on the roof? |  | Yes
Are any measures of water harvesting provided on the roof? |  | Yes
Does client/off-taker has existing waste management policy?
Is the client ready to provide material storage area during the development phase of plant? |  | Yes
Is any scrap yard available in client’s premises?
Is the structural stability of the roof rust & prominent?
Please mention: If any other Unsafe conditions observed on site |  |  |  |  | out door ahu unit, piping & cable crossing etc

## Input's from Site Visit (hidden)
Fourth Partner Energy Pvt. Ltd |  |  |  |  | DOC. No: 4PEL/DES-ISS/110 #I01, R02.
Issue Date: 11/12/2023.
Control Copy No. 02.
Inputs - Site Survey Form
DETAILED PROJECT SITE SURVEY REPORT
Client name | Metro Junction mall |  |  | Power bills | Collected
Client address | Metro Junction Mall, Kalyan - Shilphata Rd, Kalyan East, Kalyan, Maharashtra 421306 |  |  | Contract demand * | 449 KVA
Contact person name | 0 |  |  | Incommer trans. rating* | Rating- kVA
GPS Cordinates | 19.229564° N |  |  | Netmetring voltage level | 0.45 kV | Voltage level in kV | 0.45 kV
GPS Cordinates | 73.123271° E |  |  | No. of Transformer | Qty - _01 Nos | Voltage ratio | Voltage Ratio - ___/____
Mob. No. | 0 |  |  | Metering cubical (Class) | Class _____________
Mail id | 0 |  |  | ceig report | 0
Proposed Kwp | kWp MwH |  |  | Plant cad files | Available |  |  |  | Locked Cell
Project type | Capex |  |  | plant SLD cad file | Available |  |  |  | Editable cell
Power Consumptions (Min.) |  | Max. |  | Hand sketch SLD |  |  |  |  | *Mandatory
APFC availability |  | Solar termination |  | No. of locations | 1 | After Site Visit. |  |  | Drop Down
CT input for PFC |  |  |  | Best Network operator | <mention best oprator>
Metering CT& PT Details / Class | 0 |  |  | Min & Max. Weather Temp.
Plant Holiday/Power Holidays* | Days |  |  | DG capacities * | Rating - _1010 kVA
No. of service connection* | 2 |  |  | No. of DGs * | Qty - __03 Nos
PF maintaining | Power Factor: 0.89-0.995 |  |  | Reverse Protections | (Yes/No)
Any exsiting Plants | Yes | If yes | NO | Metering class | Class _____________ | rating, make ,model no. | Make: ___________________
Plant details
| Plant 1 | Plant 2 | Plant 3 | Plant 4 | Plant 5 | Plant 6 | Plant 7 | Plant 8 | Plant 9 | Plant 10 | Plant 11 | Plant 12 | Plant 13 | Plant 14 | Plant 15
Type of plant * | Shed | Shed | Shed | Shed | Shed | Shed | Shed | Shed | Shed | Shed | Ground | Ground | Ground | Ground | Ground
Electrical Details
Name of the building (As per customer's nomenclature) | Main RCC B Block at LG | Main RCC D Block at LG | Parking | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Termination distance in mtrs | 170 | 220 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tentative location of inverter & LT Panel | at terrace level | at terrace level | At parking area | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Spare feeder avilability (mention as rating) | No | No | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bus bar extensions required? Scope? | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Existing Bus Bar Size Material- Al/Cu./Type | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Main Incomer Rating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Transmission method/ Method of Cable laying | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Termination LT Panel image | Attached | Attached | Attached | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Common Inputs
Distance from the sea shore? In Km | 40km | 40km | 40km | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Earth pit location identification | South (front side) | South (front side) | At parking area | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Availability of water system/Water tank for module cleaning | Available | Available | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Type of Water / Quality of water PPM (TDS Level) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Permanent Access to roof location (None / Monkey Ladder / Step or Staricage Ladder) | Available | Available | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Scope of Roof Access | Client | Client | Client | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exisiting Lightening protection system & Coverage radius | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Parapet wall availability and Height | 1.2m | 1.2m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Presence of intermediate column, if yes, height, spacing & dimension of the column | yes, 10m & 7m | yes, 10m & 7m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water harvesting availability | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Roof penetration is allowed or not (penetration if any shall be sealed properly) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Any Observations/Remarks | intermediate columns, AHU unit, Water tank present at roof | intermediate columns, AHU unit, Water tank present at roof | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Logistic, Storage & Execution Details
Is Site reachable through road? | Plant 1: Yes; Plant 2: No
Storage Space for materials (L x W) | Plant 1: 0; Plant 2: Place; Plant 3: Distance
Can a truck of 40 feet container reach site? (Observation/Dimension/Photo) | Plant 1: 0
Can a Hydra or Crane can move around structures on side (Yes/No) East ____, West ___, North ___, South ___ Attach Photos | Plant 1: 0; Plant 2: 0; Plant 3: 0; Plant 4: 0
No of Working Hours allowed for execution? | Plant 1: 0
No of Workers allowed at Site? | Plant 1: 0
Any other restrictions related to execution | Plant 1: 0; Plant 2: 0
RCC Roof Details
Water proofing type & Thickness in mm | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Waterproofing removal permission (Yes/No) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Height of Building in mtrs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Permission for chipping | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Year of construction | 0 | 2010 around | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Roof Area (Sqm) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Roof area available for solar installation (Sqm) | 250 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Thickness of slab in mm | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Proposed structure height in mm | 3m | 3m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Shed Roof Details
Height of the building at edge in mtrs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Height of the building at ridge in mtrs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Type of Shed Asbestos/Trapezoidal sheet/Puff Sheet/Standing seam | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Thickness of roof sheet (mm) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tilt/Angle of shed | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Railing required ? | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Activities under the roof (Manufacturing, Heating work, Chemical Emission, Paint shop, others) (Capture specific activity having impact on the generation) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Distance between Machinery & Shed? Any heating furnace operations below the shed? | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Last major refurbishment (sheet change, leakage repairs, water proofing etc) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Shadow Casting Objects on or near to the roof (Trees,Buildings,Water tank, Exhaust pipes, chillers, Turbo Fan, etc) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Roof Condition (Good/Leakages / repairs / others) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Year of construction | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Skylight Nos & Dimensions in mm | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sky light to sky light distance in mm | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Existing Gutter length in mtrs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Turbo vent dimensions in mm | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Turbo vent to turbo vent distance in mm | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Any level difference in roof location (indicate location on Roof plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Additional load bearing capacity of the roof for Solar PV & installation / maintenance (Indicative distributed load capacity of 20kg/m2, point load capacity 80 kg/m2.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exisiting Lifeline / Walkway availability (indicate location on Roof plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Metal Sheet Profile Diagram
Diagram --> | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Metal Sheet & Purlin Pictures
Photo 1 --> | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Photo 2 --> | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ground Details
Is Land Clear? (Yes/No) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
If No then please mention type of obstacles | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Photo 1 --> | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Photo 2 --> | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Available Ground area in acres | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Land Levelling required? (Yes/No) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Scope of Vegetation/Trees/obstacle clearing. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Soil test report available? (Yes/No) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Scope of Soil test | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specify soil type (if possible) Wet soil/Dry soil/Hard rock/Fissured rock) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Whether Rock area? At what depth | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Undulations if any? | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Near by Lake/River passing? | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Area within client boundary (Yes/No) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Does the client require boundary/fencing (Yes/No) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Are there trees/obstacles outside client boundary causing shadows? (Yes/No) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Is there any water body/patches in land area? | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remark (If any) :- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Car Parking Details
Type of Ground Whether Tiles/ PCC/ RCC/ soil Ground | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
If RCC, Client is ready to Anchoring / Isolated foundation? | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No of Cars Parking | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Any transmission lines passing over Parking area? | 0 | 0 | 0 | 0 | 0 | 0 | Car Parking Details | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
If yellow parking markings available, Length and width of markings | 0 | paver block | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Proposed structure height in mm | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remark (If any) :- | 0 | as per area | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Floating | bar: Plant 1 to Plant 10
Type of Pond for Floating (Natural/Constructed) | Plant 1: 0
Depth of Pond? In mtrs | Plant 1: 0
Minimum Water Level that can be maintained? | Plant 1: 0; Plant 2: 0
Water Source | Plant 1: 0
Water Quality | Plant 1: 0
History of drought in last 10 Yrs | Plant 1: 0; Plant 2: 0
Bathymetric survey available? (Yes/No) | Plant 1: 0
Anchoring (Bottom/Side) | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remark (If any) :- | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SITE PHOTOS CAPTURED | bar: Plant 1 to Plant 10
Site photos from all four directions | Plant 1: Yes; Plant 2: 0; Plant 3: 0; Plant 4: 0; Plant 5: 0; Plant 6: 0; Plant 7: 0; Plant 8: 0
Photos of objects giving shadow | Plant 1: Yes; Plant 2: 0; Plant 3: 0; Plant 4: 0; Plant 5: 0; Plant 6: 0; Plant 7: 0; Plant 8: 0
Photos of LT room | Plant 1: Yes; Plant 2: 0; Plant 3: 0; Plant 4: 0; Plant 5: 0; Plant 6: 0; Plant 7: 0; Plant 8: 0
Observation / Remark for BD Team - | Plant 1: shadows of adjacent redidential tower might occure in morning hours, need to verify; Plant 2: 0; Plant 3: 0; Plant 4: 0; Plant 5: 0; Plant 6: 0; Plant 7: 0; Plant 8: 0
Documents to be collected | bar: Plant 1 to Plant 10
1. SLD of the facility | Plant 1: 0; Plant 4: 3. DG Running Data; Plant 6: 0
2. Roof Plan / Roof Structure Drawings | Plant 1: 0; Plant 4: 4. Electricity Bills; Plant 6: Yes
5. Soil test report | Plant 1: 0; Plant 4: 6. CEIG approved Existing drawings; Plant 6: 0
7. SEZ/ SEZ approval | Plant 1: 0; Plant 4: 8. Structure Stability report; Plant 6: 0
9. HSE/Safety Policy | Plant 1: 0
Minutes of the Meeting | bar: Plant 1 to Plant 10
Key Action Points | Plant 1: - Total required capacity is 400kWp - total capacity is to be terminated into 4 diffent panels as below. i)Block D, ii)Block B, iii)Zingverse iv)Zingeria - accordingly 4 diff inverters, LT panels, generation meters need to consider
Name of the Surveyor & Signature | Plant 1: 0; Plant 4: Name of Customer & Signature
Comments(if any):
Client scope
Already exist
4PEL Scope
Not Required
Client scope
4PEL Scope
PUF sheet
Tin sheet
|  | Client scope |  |  |  | CT&PT Required
| RCC | Already exist |  |  |  | CT&PT Not Required
| Shed |  |  |  |  | CT&PT Indoor type
| Ground |  |  |  |  | CT&PT Outdoor type
| Floating | 4PEL Scope
Not Required
| Yes | 4PEL scope
| No | Client scope
| LT | Required
| HT | Not Required
Aluminium(Al)
Copper(Cu)
Before APFC | Plant 2: UG Trench
After APFC | Plant 2: Client scope
Existing Trench
Cable Tray
Not Required
Wet soil
Dry soil
Hard rock
Fussured rock
Yes
No
Client Will Arrange
Collected
Not collected
Client will send by mail

## Site Vist fomat (Design)
Fourth Partner Energy Pvt. Ltd. |  |  |  | DOC. No: | 4PEL/DES-SSR/553 #I01, R00.
|  |  |  | Issue Date : | 11/12/2023.
|  |  |  | Control Copy No : | 2
SITE SURVEY REPORT |  |  |  | Survey Date : | 2026-05-11
General Information
Name of the Customer | Metro Junction mall
Contact Person's Name & Designation |  |  | Mobile No |  | Email Id
Site Address : | Metro Junction Mall, Kalyan - Shilphata Rd, Kalyan East, Kalyan, Maharashtra 421306
GPS Cordinates | 19.229564° N | 73.123271° E | Nearest Railway Station | Kalyan | Nearest Highway | Kalyan-Shil phata
Industry Type | Cement/Paint/FMCG/Metal/ITES/Auto & Auto Ancillary/Textile/Pharma/Plastic& Rubber/Infra/Telecom/Financial Srevices/Others (Specify) - Mall
Type of business operation at site | Manufacturing | Warehousing | Packaging | Retail | Service | Others (Specify) - Mall
Type of Installation |  | RCC |  | Parking
Ownership | Owned | Leased | Lease expiry after yrs | Right to Install SPP --> | Yes | No
Customer RE Requirement
Expected Solar PV / Storage Capacity | kWp MwH | CT | Gross Metering | Captive | On Grid | Off Grid
Proposed SPP Evacuation Voltage | 0.45 kV | (If Evacuation Voltage >=11 KV, check space available to construct substation)
Existing Electrical Infrastructure
Discom Name | MSEDCL | Contract Demand | 449 KVA | Total Connected Load | kW | Power Factor: 0.89-0.995
Distribution Transformer (DT) Details | Qty - _01 Nos | Rating- kVA | Voltage Ratio - ___/____ | Vector Group- _______ | Shortcircuit Level (HT VCB Level) - _______ Kv | Make & Model for each transformer -
Sources of Power Available for synchronizing | EB Supply | DG Supply | CPP | Others (specify) | Synchronisation | Manual/Automatic - Automatic
Grid Outage Data | No. of Hours/day :__________ | Operational Days in a Year | Days | Grid Frequency/Voltage Fluctuations (Yes/No) | Yes | No
| No. of times/Day: ______________ | No of Off Days for Maintenance & Load | Days | kW | Operational Hours in a Day: ________ | No of Shifts/Day: __________
No of Off Days for Holidays & Load | Days | kW | Installed DG Set | Qty - __03 Nos | Rating - _1010 kVA | Voltage _400 V
Existing Solar Capacity in KWp (DC capacity) | NO | 0 | Is the existing plant Net Metered? | (Yes/No) | Is the existing plant installed with RPR? | (Yes/No)
EB Meter Details | Class _____________ | Make: ___________________ | STC Rating ____________ | APFC Panel (Location & Rating) type( automatice/manual)
No. of service connection (Qty.) | 2 | Metering CT& PT Details / Class |  | Earth resistivity & Standards/Specifications | 2 ohm- convetional type/ chemical
Electrical Details | [6 empty] | Electrical Details
Name of the building (As per customer's nomenclature) | Main RCC B Block at LG | Main RCC D Block at LG | Parking
Location wise Exisiting LT panel breker capacity | LT Room B Block at LG Main termination is in Ground floor | LT Room D Block at LG Main termination is in Ground floor | LT Room B Block at LG Main termination is in Ground floor
Incomer Cable runs and size
Termination distance in mtrs | 170 | 220 | 200
Tentative location of inverter & LT Panel | at terrace level | at terrace level | At parking area
Spare feeder avilability (mention as rating) | No | No | No
Bus bar extensions required? Scope?
Existing Bus Bar Size Material- Al/Cu./Type
Main Incomer Rating
Transmission method/ Method of Cable laying
Termination LT Panel image | Attached | Attached | Attached
Common Inputs | [6 empty] | Commen inputs
Distance from the sea shore? In Km | 40km | 40km | 40km
Earth pit location identification | South (front side) | South (front side) | At parking area
Availability of water system/Water tank for module cleaning | Available | Available
Type of Water / Quality of water PPM (TDS Level)
Permanent Access to roof location (None / Monkey Ladder / Step or Staricage Ladder) | Available | Available | NA
Scope of Roof Access | Client | Client | Client
Exisiting Lightening protection system & Coverage radius
Parapet wall availability and Height | 1.2m | 1.2m
Presence of intermediate column, if yes, height, spacing & dimension of the column | yes, 10m & 7m | yes, 10m & 7m
Water harvesting availability
Roof penetration is allowed or not (penetration if any shall be sealed properly)
Any Observations/Remarks | intermediate columns, AHU unit, Water tank present at roof | intermediate columns, AHU unit, Water tank present at roof
RCC Roof Details | [6 empty] | RCC Roof details
Water proofing type & Thickness in mm
Waterproofing removal permission (Yes/No)
Height of Building in mtrs
Permission for chipping
Year of construction |  | 2010 around
Roof Area (Sqm)
Roof area available for solar installation (Sqm) | 250 | 2030
Near by obj. moving shadow | mall buidling | theatre shed, dome, tanks, adjacent building
Thickness of slab in mm
Proposed structure height in mm | 3m | 3m
Shed Roof Details | [6 empty] | Shed Roof details
Height of the building at edge in mtrs
Height of the building at ridge in mtrs
Type of Shed Asbestos/Trapezoidal sheet/Puff Sheet/Standing seam
Thickness of roof sheet (mm)
Tilt/Angle of shed
Railing required ?
Activities under the roof (Manufacturing, Heating work, Chemical Emission, Paint shop, others) (Capture specific activity having impact on the generation)
Distance between Machinery & Shed? Any heating furnace operations below the shed?
Last major refurbishment (sheet change, leakage repairs, water proofing etc)
Shadow Casting Objects on or near to the roof (Trees,Buildings,Water tank, Exhaust pipes, chillers, Turbo Fan, etc)
Roof Condition (Good/Leakages / repairs / others)
Year of construction
Skylight Nos & Dimensions in mm
Sky light to sky light distance in mm
Existing Gutter length in mtrs
Turbo vent dimensions in mm
Turbo vent to turbo vent distance in mm
Any level difference in roof location (indicate location on Roof plan)
Additional load bearing capacity of the roof for Solar PV & installation / maintenance (Indicative distributed load capacity of 20kg/m2, point load capacity 80 kg/m2.)
Exisiting Lifeline / Walkway availability (indicate location on Roof plan)
| Metal Sheet Profile Diagram | Metal Sheet Profile Diagram | Metal Sheet Profile Diagram | Metal Sheet Profile Diagram | Metal Sheet Profile Diagram | Metal Sheet Profile Diagram | Metal Sheet Profile Diagram | Metal Sheet Profile Diagram | Metal Sheet Profile Diagram | Metal Sheet Profile Diagram | Metal Sheet Profile Diagram | Metal Sheet Profile Diagram | Metal Sheet Profile Diagram | Metal Sheet Profile Diagram | Metal Sheet Profile Diagram
Diagram -->
| Metal Sheet & Purlin Pictures | Metal Sheet & Purlin Pictures | Metal Sheet & Purlin Pictures | Metal Sheet & Purlin Pictures | Metal Sheet & Purlin Pictures | Metal Sheet & Purlin Pictures | Metal Sheet & Purlin Pictures | Metal Sheet & Purlin Pictures | Metal Sheet & Purlin Pictures | Metal Sheet & Purlin Pictures | Metal Sheet & Purlin Pictures | Metal Sheet & Purlin Pictures | Metal Sheet & Purlin Pictures | Metal Sheet & Purlin Pictures | Metal Sheet & Purlin Pictures
Photo 1 -->
Photo 2 -->
Ground Details | [6 empty] | Ground Details
Is Land Clear? (Yes/No)
If No then please mention type of obstacles
Photo 1 -->
Photo 2 -->
Available Ground area in acres
Land Levelling required? (Yes/No)
Scope of Vegetation/Trees/obstacle clearing.
Perminsion of Vegetation/Trees/obstacle clearing.
Soil test report available? (Yes/No)
Scope of Soil test
Specify soil type (if possible) Wet soil/Dry soil/Hard rock/Fissured rock)
Whether Rock area? At what depth
Undulations if any?
Near by Lake/River passing?
Area within client boundary (Yes/No)
Does the client require boundary/fencing (Yes/No)
Are there trees/obstacles outside client boundary causing shadows? (Yes/No)
Is there any water body/patches in land area?
Flooding Area? Yes/No. If Yes, at what height and Period of Flooding
Remark (If any) :-
Car Parking Details | [6 empty] | Car Parking Details
Type of Ground Whether Tiles/ PCC/ RCC/ soil Ground |  | paver block
If RCC, Client is ready to Anchoring / Isolated foundation?
No of Cars Parking |  | as per area
Any transmission lines passing over Parking area? |  | No
If yellow parking markings available, Length and width of markings |  | No
Proposed structure height in mm |  | 2500-3000
Remark (If any) :- |  | shadow of mall building need to check
Floating Details
Type of Pond for Floating (Natural/Constructed) |  | Depth of Pond? In mtrs |  | Minimum Water Level that can be maintained?
Water Source |  | Water Quality |  | History of drought in last 10 Yrs
Bathymetric survey available? (Yes/No) |  | Anchoring (Bottom/Side)
Remark (If any) :-
Logistic, Storage & Execution Details
Is Site reachable through road? | Yes | No | Storage Space for materials (L x W) |  | Place | Distance
Can a truck of 40 feet container reach site? (Observation/Dimension/Photo) |  | Can a Hydra or Crane can move around structures on side (Yes/No) East ____, West ___, North ___, South ___ Attach Photos
No of Working Hours allowed for execution? |  | No of Workers allowed at Site? |  | Any other restrictions related to execution
Site Captured Photos
Site photos from all four directions | Yes
Photos of objects giving shadow | Yes
Photos of LT room | Yes
Observation / Remark for BD Team - | shadows of adjacent redidential tower might occure in morning hours, need to verify
Documents to be collected
Name of the Documents | Collected (Yes/No) | Name of the Documents | Collected (Yes/No) | Name of the Documents | Collected (Yes/No)
1. SLD of the facility |  | 2. Roof Plan / Roof Structure Drawings |  | 3. DG Running Data
4. Electricity Bills | Yes | 5. Soil test report |  | 6. CEIG approved Existing drawings
7. SEZ/ SEZ approval |  | 8. Structure Stability report |  | 9. HSE/Safety Policy
Minutes of Meeting
Key Action Points | - Total required capacity is 400kWp - total capacity is to be terminated into 4 diffent panels as below. i)Block D, ii)Block B, iii)Zingverse iv)Zingeria - accordingly 4 diff inverters, LT panels, generation meters need to consider
Name of the Surveyor & Signature |  |  | Name of Customer & Signature
| Shed | RCC | Ground | Parking | Floating | Other

## Input's from Initial Design
|  | Fourth Partner Energy Pvt. Ltd | [13 empty] | DOC. No: 4PEL/DES-IDS/039 #I01, R05.
Issue Date: 23/02/2026.
Control Copy No. 02.
Initial Design Sheet
DETAILED INITIAL DESIGN REPORT | [10 empty] | Please fill Existing Plant details | Inputs for initial design from BD |  |  |  |  | Information Sheet (String Inv. LT)
Availability of RFP/RFQ |  | Yes |  |  | Is Design prepared According to RFP/RFQ |  |  | Yes |  |  |  | Module wattage (Wp) |  | 595 / 590 / 585
Site Name & State |  | Metro Junction mall |  |  | Maharashtra |  |  | Comment |  |  |  | Module Origin |  | ALMM Approved |  |  | Shed | 0
Address & Lat Long |  | Metro Junction Mall, Kalyan - Shilphata Rd, Kalyan East, Kalyan, Maharashtra 421306 |  |  | 19°13'45.98"N 73°07'23.94"E | [6 empty] | Prefered Inverter make |  | Solis / Sungrow / Equivalent |  |  | Long Rail | 0
Approval Details |  | Name of the Person |  |  | Approval Date | [6 empty] | DC/AC Ratio |  | 0 |  |  | RCC | 0
Initial Design Done By |  | Ashish A |  |  | Date: | 2026-06-26 | [5 empty] | Roof Puncturing permission from client |  |  |  |  | RCC Raised | 400.52
Initial Design Approved By |  | Sagar C |  |  |  | 2026-06-26 | [5 empty] | Modules (MMS) |  | 0 |  |  | RCC Raised on Pillars | 0
[12 empty] | Lifeline location |  | 0 |  |  | Ground Mounted | 0
Revision No. |  | DR1 * | DR2 * | DR3 * | DR4 * | DR5 * | DR6 * | Notes for Design from BD |  |  |  | Walkway Dimension (W) |  | 0 |  |  | Parking- Car/Bike | 0
Receive date |  | 2026-05-21 | 2026-06-04 | 2026-06-26 |  |  |  | 0 |  |  |  | Anchoring permission for RCC |  | 0 |  |  | Parking-Truck/Bus | 0
Reason for Revision |  | Initial Design | Capacity increased | AS per client reuirement layout revised | [7 empty] | PV Syst |  | 0 |  |  | Floating | 0
[17 empty] | Total Capacity | 400.52
Date of Sent |  | 2026-05-22 | 2026-06-04 | 2026-06-26
[18 empty] | Inverter Over loading indication |  |  | NIL | 0 to 1 | 1 to 1.25
[21 empty] | 1.25-1.4 | 1.4-1.45 | Above 1.45
String Inverter Initial Design |  |  | Module Make & Origin |  | Renewsys | Indian ALMM |  |  |  |  | Select the Optimazer Model for Solar edge inverter |  |  | Optimizers- Model-S 1400/ S 1500 |  |  |  | Module Tilt |  |  | < 5 | < 8 | > 8 |  | Click to check the Earth strip selection | [9 empty] | Consider Railings for Module tilt >=8
|  |  | Module Wattage |  | 620 | Wp
Sl.No | Building/Location Name | Type of Installation | Type of sheet | Available Modules | No. of Modules Utilized | DC Capacity in kWp | Solis | [9 empty] | AC Capacity in kW | Inverter Overloading DC/AC Ratio |  |  | Common item for Rooftop and Ground mounted | [19 empty] | For Rooftop site's | [11 empty] | For Ground Mounted Site's
[7 empty] | 150 | 125 | 80 | 60 | 50 | 30 | 25 | 20 | 15 | 10 |  |  |  |  | Total No. of strings | Module Tilt in Degree | Structure clearance in mm | Earth strip Length in Mtrs (MMS) | Earth strip size (MMS) | Earth strip Length in Mtrs (INV) | Earth strip size (INV) | Earth strip Length in Mtrs (ACCB PANEL) | Earth strip size (ACCB PANEL) | Earth strip Length in Mtrs (LA) | Earth strip size (LA) | Type of Lightening Arrestor | No. of LA's (Qty.) | Water pipe line in Mtrs | Walkway in Mtrs | Railings in Mtrs | Lifeline Rope in Rmtrs | No. of Lifeline Post (Qty.) | DC Cable Length in Mtrs 4 Sqmm | DC Cable Length in Mtrs 6 Sqmm | DC cable tray length in Mtrs 50x50x2mm | DC cable tray length in Mtrs 100x50x2mm | Zero Degree Walkways in Mtrs | Step Walkway in Mtrs | Gutter length for harvesting in Mtrs | Skylight Width in mm | Skylight Length in Run. Mtrs | Turbo Vent Qty. | Roof monitor cross over (Qty.) | Ladder for Roof to roof Height in Mtrs | Type of Ladder | Building Height in Mtrs | Total Plant Area in Acrs | DWC pipe for DC cable in Mtrs | Approach Road in Mtrs | Internal Road in Mtrs | Strom Water Drainage in Mtrs | Peripheral Length in Mtrs | Peripheral Road in Mtrs
1 | Main RCC B Block at LG South side | RCC Raised |  | 646 | 646 | 400.52 | 2 | [9 empty] | 300 | 1.3351 |  |  | 33 | 5 | 3000 mm | 640 | 25x3mm | 262 | 25x3mm | 122 | 25x3mm | 120 | 25x6mm | ESE 107 Mtrs Radius | 1 | 408 | 350 | 0 | 350 | 51 | 4050 | 0 | 350 | 0 | [9 empty] | 0 |  |  |  |  | 0
2 | LT Panel - 2 |  |  |  |  | 0 | [10 empty] | 0 | #DIV/0! | [33 empty] | 0 |  |  |  |  | 0
3 | [5 empty] | 0 | [10 empty] | 0 | #DIV/0! | [33 empty] | 0 |  |  |  |  | 0
4 | [5 empty] | 0 | [10 empty] | 0 | #DIV/0! | [33 empty] | 0 |  |  |  |  | 0
5 | [5 empty] | 0 | [10 empty] | 0 | #DIV/0! | [33 empty] | 0 |  |  |  |  | 0
6 | [5 empty] | 0 | [10 empty] | 0 | #DIV/0! | [33 empty] | 0 |  |  |  |  | 0
7 | [5 empty] | 0 | [10 empty] | 0 | #DIV/0! | [33 empty] | 0 |  |  |  |  | 0
8 | [5 empty] | 0 | [10 empty] | 0 | #DIV/0! | [33 empty] | 0 |  |  |  |  | 0
9 | [5 empty] | 0 | [10 empty] | 0 | #DIV/0! | [33 empty] | 0 |  |  |  |  | 0
10 | [5 empty] | 0 | [10 empty] | 0 | #DIV/0! | [33 empty] | 0 |  |  |  |  | 0
11 | [5 empty] | 0 | [10 empty] | 0 | #DIV/0! | [33 empty] | 0 |  |  |  |  | 0
12 | [5 empty] | 0 | [10 empty] | 0 | #DIV/0! | [33 empty] | 0 |  |  |  |  | 0
13 | [5 empty] | 0 | [10 empty] | 0 | #DIV/0! | [33 empty] | 0 |  |  |  |  | 0
14 | [5 empty] | 0 | [10 empty] | 0 | #DIV/0! | [33 empty] | 0 |  |  |  |  | 0
15 | [5 empty] | 0 | [10 empty] | 0 | #DIV/0! | [33 empty] | 0 |  |  |  |  | 0
16 | [5 empty] | 0 | [10 empty] | 0 | #DIV/0! | [33 empty] | 0 |  |  |  |  | 0
17 | [5 empty] | 0 | [10 empty] | 0 | #DIV/0! | [33 empty] | 0 |  |  |  |  | 0
18 | [5 empty] | 0 | [10 empty] | 0 | #DIV/0! | [33 empty] | 0 |  |  |  |  | 0
19 | [5 empty] | 0 | [10 empty] | 0 | #DIV/0! | [33 empty] | 0 |  |  |  |  | 0
20 | [5 empty] | 0 | [10 empty] | 0 | #DIV/0! | [33 empty] | 0 |  |  |  |  | 0
21 | [5 empty] | 0 | [10 empty] | 0 | #DIV/0! | [33 empty] | 0 |  |  |  |  | 0
22 | [5 empty] | 0 | [10 empty] | 0 | #DIV/0! | [33 empty] | 0 |  |  |  |  | 0
23 | [5 empty] | 0 | [10 empty] | 0 | #DIV/0! | [33 empty] | 0 |  |  |  |  | 0
24 | [5 empty] | 0 | [10 empty] | 0 | #DIV/0! | [33 empty] | 0 |  |  |  |  | 0
25 | [5 empty] | 0 | [10 empty] | 0 | #DIV/0! | [33 empty] | 0 |  |  |  |  | 0
26 | [5 empty] | 0 | [10 empty] | 0 | #DIV/0! | [33 empty] | 0 |  |  |  |  | 0
27 | [5 empty] | 0 | [10 empty] | 0 | #DIV/0! | [33 empty] | 0 |  |  |  |  | 0
28 | [5 empty] | 0 | [10 empty] | 0 | #DIV/0! | [33 empty] | 0 |  |  |  |  | 0
29 | [5 empty] | 0 | [10 empty] | 0 | #DIV/0! | [33 empty] | 0 |  |  |  |  | 0
30 | [5 empty] | 0 | [10 empty] | 0 | #DIV/0! | [33 empty] | 0 |  |  |  |  | 0
Total |  |  |  | 646 | 646 | 400.52 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 1.3351 |  |  | 33 | [11 empty] | 1 | 408 | 350 | 0 | 350 | 51 | 4050 | 0 | 350 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | Per Wp cost of Inverter | [8 empty] | 1.4981
[19 empty] | IN : | 1 OUT
| AC cable length from INV. To ACCB Panel | [18 empty] | Inv count | Inv. Combination (reference) | AC Capacity in KW | Termination Distance as per site survey report | No. of Runs | Total running mtrs. | Selected Cable Size | Cable transmission method | [5 empty] | ACCB Panels Details
| Building/Location Name | Distance/Runs/ Cable Size | Inverter-1 | Inverter-2 | Inverter-3 | Inverter-4 | Inverter-5 | Inverter-6 | Inverter-7 | Inverter-8 | Inverter-9 | Inverter-10 | Inverter-11 | Inverter-12 | Inverter-13 | Inverter-14 | Inverter-15 | Cable tray From Inv. To ACCB Panel in mtrs | LT combination count | [6 empty] | Note: If no match pls increase runs | New cable tray in mtrs | Soil trench in mtrs | Road Crossing | Existing cable tray in mtrs | Cable Gantry in mtrs |  | Sl. No. | Name of the Locations (Building) | Inv. Combination IN & OUT | ACCB Panel Capacity |  | ACCB Panel Current rating | ACCB Panel Quantity
| Main RCC B Block at LG South side | Cable length in mtrs | 10 | [14 empty] | 10 | 1 | 1 | 1 IN :1 OUT | 150 | 170 | 1 | 170 | 3.5CX300Sqmm | 170 | 0 | 0 | 0 | 0 |  | 1 |  | 1 IN : 1 OUT | 10/15/20/25/30/33/50/60/66KW |  | 15A-90A | 0
|  | Cable size in sqmm | 3.5CX300Sqmm | [14 empty] | 100x75x2mm | [8 empty] | 100x75x2mm | [5 empty] | 2 |  | 2 IN : 1 OUT | 10/15/20/25/30/50/60/66KW |  | 15A-90A | 0
| LT Panel - 2 | Cable length in mtrs | 10 | [14 empty] | 10 | 2 | 1 | 1 IN :1 OUT | 150 | 220 | 2 | 440 | 3.5CX185Sqmm | 220 | 0 | 0 | 0 | 0 |  | 3 |  | 3 IN : 1 OUT | 15/30/35/50/60/70/80/90/99KW |  | 25A-130A | 0
|  | Cable size in sqmm | 3.5CX300Sqmm | [14 empty] | 100x75x2mm | [8 empty] | 200x75x2mm | [5 empty] | 4 | Main RCC B Block at LG South side (2 in 1 out) | 1 IN : 1 OUT | 80/125/150KW |  | 110A-155A | 2
| 0 | Cable length in mtrs | [16 empty] | 3 | 0 | 0 IN :1 OUT |  | 200 |  | 0 | #DIV/0! | [6 empty] | 5 |  | 2 IN : 1 OUT | 100/110/120KW | 100KW | 135A- 165A | 0
|  | Cable size in sqmm | [30 empty] | 6 |  | 2 IN : 1 OUT | 110/120/130/133/150/160/170KW | 100KW | 155A- 230A | 0
| 0 | Cable length in mtrs | [16 empty] | 4 | 0 | 0 IN :1 OUT |  | 0 |  | 0 | #DIV/0! | [6 empty] | 7 |  | 2 IN : 1 OUT | 200-220KW | 150KW | 265A- 300A | 0
|  | Cable size in sqmm | [30 empty] | 8 |  | 3 IN : 1 OUT | 250-270KW | 150KW | 330A- 370A | 0
| 0 | Cable length in mtrs | [16 empty] | 5 | 0 | 0 IN :1 OUT |  | 0 |  | 0 | #DIV/0! | [6 empty] | 9 |  | 3 IN : 1 OUT | 300-330KW | 150KW | 400A- 450A | 0
|  | Cable size in sqmm | [30 empty] | 10 |  | 4 IN : 1 OUT | 330-370KW |  | 450A- 500A | 0
| 0 | Cable length in mtrs | [16 empty] | 6 | 0 | 0 IN :1 OUT |  | 0 |  | 0 | #DIV/0! | [6 empty] | 11 |  | 4 IN : 1 OUT | 400-440KW |  | 500A- 600A | 0
|  | Cable size in sqmm | [30 empty] | 12 |  | 5 IN : 1 OUT | 450-490KW |  | 600A- 650A | 0
| 0 | Cable length in mtrs | [16 empty] | 7 | 0 | 0 IN :1 OUT |  | 0 |  | 0 | #DIV/0! | [6 empty] | 13 |  | 5 IN : 1 OUT | 500-550KW |  | 670A- 730A | 0
|  | Cable size in sqmm | [30 empty] | 14 |  | 6 IN : 1 OUT | 560-600KW |  | 740A- 800A | 0
| 0 | Cable length in mtrs | [16 empty] | 8 | 0 | 0 IN :1 OUT |  | 0 |  | 0 | #DIV/0! | [6 empty] | 15 |  | 6 IN : 1 OUT | 600-660KW |  | 800A- 880A | 0
|  | Cable size in sqmm | [30 empty] | 16 |  | 7 IN : 1 OUT | 670-710KW |  | 900A- 950A | 0
| 0 | Cable length in mtrs | [16 empty] | 9 | 0 | 0 IN :1 OUT |  | 0 |  | 0 | #DIV/0! | [6 empty] | 17 |  | 7 IN : 1 OUT | 700-770KW |  | 950A-1050A | 0
|  | Cable size in sqmm | [30 empty] | 18 |  | 8 IN : 1 OUT | 780-820KW |  | 1050A-1100A | 0
| 0 | Cable length in mtrs | [16 empty] | 10 | 0 | 0 IN :1 OUT |  | 0 |  | 0 | #DIV/0! | [6 empty] | 19 |  | 8 IN : 1 OUT | 800-880KW |  | 1100A- 1200A | 0
|  | Cable size in sqmm | [30 empty] | 20 |  | 9 IN : 1 OUT | 890-940KW |  | 1200A- 1250A | 0
| 0 | Cable length in mtrs | [16 empty] | 11 | 0 | 0 IN :1 OUT |  | 0 |  | 0 | #DIV/0! | [6 empty] | 21 |  | 9 IN : 1 OUT | 900-990KW |  | 1250A- 1300A | 0
|  | Cable size in sqmm | [30 empty] | 22 |  | 10 IN : 1 OUT | 1000-1100KW |  | 1320A- 1450A | 0
| 0 | Cable length in mtrs | [16 empty] | 12 | 0 | 0 IN :1 OUT |  | 0 |  | 0 | #DIV/0! | [6 empty] | 23 |  | 10 IN : 1 OUT | 1000-1150KW |  | 1320A- 1500A | 0
|  | Cable size in sqmm | [30 empty] | 24 |  | 11 IN : 1 OUT | 1100-1210KW |  | 1450A- 1600A | 0
| 0 | Cable length in mtrs | [16 empty] | 13 | 0 | 0 IN :1 OUT |  | 0 |  | 0 | #DIV/0! | [6 empty] | 25 |  | 11 IN : 1 OUT | 1220-1260KW |  | 1600A-1660A | 0
|  | Cable size in sqmm | [30 empty] | 26 |  | 12 IN : 1 OUT | 1200-1320KW |  | 1600A-1750A | 0
| 0 | Cable length in mtrs | [16 empty] | 14 | 0 | 0 IN :1 OUT |  | 0 |  | 0 | #DIV/0! | [6 empty] | 27 |  | 12 IN : 1 OUT | 1330-1370KW |  | 1750A- 1800A | 0
|  | Cable size in sqmm | [30 empty] | 28 |  | 13 IN : 1 OUT | 1300-1430KW |  | 1750A- 1900A | 0
| 0 | Cable length in mtrs | [16 empty] | 15 | 0 | 0 IN :1 OUT |  | 0 |  | 0 | #DIV/0! | [6 empty] | 29 |  | 13 IN : 1 OUT | 1440-1480KW |  | 1900A- 2000A | 0
|  | Cable size in sqmm | [30 empty] | 30 |  | 14 IN : 1 OUT | 1400-1540KW |  | 2000A- 2100A | 0
| 0 | Cable length in mtrs | [16 empty] | 16 | 0 | 0 IN :1 OUT |  | 0 |  | 0 | #DIV/0! | [6 empty] | 31 |  | 14 IN : 1 OUT | 1550-1590KW |  | 2100A- 2150A | 0
|  | Cable size in sqmm | [30 empty] | 32 |  | 15 IN : 1 OUT | 1500-1650KW |  | 2100A- 2200A | 0
| 0 | Cable length in mtrs | [16 empty] | 17 | 0 | 0 IN :1 OUT |  | 0 |  | 0 | #DIV/0! | [6 empty] | 33 |  | 15 IN : 1 OUT | 1660-1700KW |  | 2200A-2300A | 0
|  | Cable size in sqmm | [30 empty] | Total ACCB Qty. | [5 empty] | 2
| 0 | Cable length in mtrs | [16 empty] | 18 | 0 | 0 IN :1 OUT |  | 0 |  | 0 | #DIV/0!
Cable size in sqmm
| 0 | Cable length in mtrs | [16 empty] | 19 | 0 | 0 IN :1 OUT |  | 0 |  | 0 | #DIV/0! | [6 empty] | Inv. To ACCB Panel Cable Calculation
|  | Cable size in sqmm | [30 empty] | Inverter Capacity |  | Inv. To ACCB Panel Distance |  |  | No.of Runs
| 0 | Cable length in mtrs | [16 empty] | 20 | 0 | 0 IN :1 OUT |  | 0 |  | 0 | #DIV/0! | [6 empty] | 150 |  | 25 |  |  | 1
|  | Cable size in sqmm | [30 empty] | Suitable Cable Size |  | 1 Runs of 300 Sq. mm
| 0 | Cable length in mtrs | [16 empty] | 21 | 0 | 0 IN :1 OUT |  | 0 |  | 0 | #DIV/0!
Cable size in sqmm
| 0 | Cable length in mtrs | [16 empty] | 22 | 0 | 0 IN :1 OUT |  | 0 |  | 0 | #DIV/0! | [6 empty] | Command if any:
|  | Cable size in sqmm | [30 empty] | 1. Structure height we have considered 4 Mtrs elevated on RCC roof & it is in Client scope conveyed by BD. 2. Designs are made as per Client shared drawings, Google earth pro data reference, actual may get vary. Shadow free timings considered from 10:30AM - 16:00PM. 3. Shadow free area can be seen after 10:30AM - 16:00PM, until shadow impact will be seen completely on the proposed location. 4. Depends on pillars & sheds below the modules, structure beneath capacity may get vary. 5. Ladders of 3 Nos of 4Mtrs height considered for modules cleaning & Other O&M activities, In FPEL scope 6. Anchoring to the master slab permission is mandatory for structure mounting. 7. Two generation panels need to consider at Block - B. 8. Height variations of all the obstacles & blocks on the proposed location area considered tentatively, this may get vary from actual site level. 9. Some installed area modules may get affected to shadow imapact due to this those modules will get hotspot in future, same need to inform to customer & if this project is in capex mode then only we can proceed with this shadow timings. Otherwise not suggestable. 10. As per client requirement modules placed above the Ducts, pipelines & above the sheds according to that client need to arrange for structure foundation. 11. Client need to confirm on Structure erection scope (i.e., in Client scope or in FPEL scope)
| 0 | Cable length in mtrs | [16 empty] | 23 | 0 | 0 IN :1 OUT |  | 0 |  | 0 | #DIV/0!
Cable size in sqmm
| 0 | Cable length in mtrs | [16 empty] | 24 | 0 | 0 IN :1 OUT |  | 0 |  | 0 | #DIV/0!
Cable size in sqmm
| 0 | Cable length in mtrs | [16 empty] | 25 | 0 | 0 IN :1 OUT |  | 0 |  | 0 | #DIV/0!
Cable size in sqmm
| 0 | Cable length in mtrs | [16 empty] | 26 | 0 | 0 IN :1 OUT |  | 0 |  | 0 | #DIV/0!
Cable size in sqmm
| 0 | Cable length in mtrs | [16 empty] | 27 | 0 | 0 IN :1 OUT |  | 0 |  | 0 | #DIV/0!
Cable size in sqmm
| 0 | Cable length in mtrs | [16 empty] | 28 | 0 | 0 IN :1 OUT |  | 0 |  | 0 | #DIV/0!
Cable size in sqmm
| 0 | Cable length in mtrs | [16 empty] | 29 | 0 | 0 IN :1 OUT |  | 0 |  | 0 | #DIV/0!
Cable size in sqmm
| 0 | Cable length in mtrs | [16 empty] | 30 | 0 | 0 IN :1 OUT |  | 0 |  | 0 | #DIV/0!
Cable size in sqmm
[28 empty] | 0 | 0 | 0 | 0
|  | Main RCC B Block at LG South side |  | LT Panel - 2 |  | 0 |  | 0 |  | 0 |  |  |  | Type of installation | Structure clearance
|  | 16 | 0 | 16 | 0 | 16 | 0 | 16 | 0 | 16 | 0 | [10 empty] | Earth Strip Qty (MMS) | [6 empty] | LT PANEL prices
|  | 25 | 0 | 25 | 0 | 25 | 0 | 25 | 0 | 25 | 0 |  |  | Shed | 100 mm | [6 empty] | 25x3mm | 640 | [5 empty] | Price per LT Panel | Total Price
|  | 35 | 0 | 35 | 0 | 35 | 0 | 35 | 0 | 35 | 0 |  |  | Long Rail | 100 mm | [6 empty] | 25x6mm | 0
|  | 50 | 0 | 50 | 0 | 50 | 0 | 50 | 0 | 50 | 0 |  |  | RCC | 500 mm | [6 empty] | 40x6mm | 0 | [5 empty] | 97834 | 0
|  | 70 | 0 | 70 | 0 | 70 | 0 | 70 | 0 | 70 | 0 |  |  | RCC Raised | 3000 mm | [6 empty] | 50x6mm | 0 | [5 empty] | 146867 | 0
|  | 95 | 0 | 95 | 0 | 95 | 0 | 95 | 0 | 95 | 0 |  |  | RCC Raised on Pillars | 3000 mm | [13 empty] | 165000 | 0
|  | 120 | 0 | 120 | 0 | 120 | 0 | 120 | 0 | 120 | 0 |  |  | Ground Mounted | 500 mm | [6 empty] | Earth Strip Qty (INV) | [6 empty] | 172168 | 344336
|  | 150 | 0 | 150 | 0 | 150 | 0 | 150 | 0 | 150 | 0 |  |  | Parking- Car/Bike | 3000 mm | [6 empty] | 25x3mm | 262 | [5 empty] | 210058 | 0
|  | 185 | 0 | 185 | 0 | 185 | 0 | 185 | 0 | 185 | 0 |  |  | Parking-Truck/Bus | 6000 mm | [6 empty] | 25x6mm | 0 | [5 empty] | 225421 | 0
|  | 240 | 0 | 240 | 0 | 240 | 0 | 240 | 0 | 240 | 0 |  |  | Floating | 0 mm | [6 empty] | 40x6mm | 0 | [5 empty] | 250802 | 0
|  | 300 | 10 | 300 | 10 | 300 | 0 | 300 | 0 | 300 | 0 | [10 empty] | 50x6mm | 0 | [5 empty] | 339020 | 0
|  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [18 empty] | 400670 | 0
|  | 16 | 0 | 16 | 0 | 16 | 0 | 16 | 0 | 16 | 0 | [10 empty] | Earth Strip Qty (LT panel) | [6 empty] | 462121 | 0
|  | 25 | 0 | 25 | 0 | 25 | 0 | 25 | 0 | 25 | 0 |  |  |  |  | Skylight mesh details | [5 empty] | 25x3mm | 122 | [5 empty] | 482550 | 0
|  | 35 | 0 | 35 | 0 | 35 | 0 | 35 | 0 | 35 | 0 |  |  |  |  | <500mm | 0 |  |  |  |  | 25x6mm | 0 | [5 empty] | 562085 | 0
|  | 50 | 0 | 50 | 0 | 50 | 0 | 50 | 0 | 50 | 0 |  |  |  |  | 500-1000mm | 0 |  |  |  |  | 40x6mm | 0 | [5 empty] | 618398 | 0
|  | 70 | 0 | 70 | 0 | 70 | 0 | 70 | 0 | 70 | 0 |  |  |  |  | 1000-1500mm | 0 |  |  |  |  | 50x6mm | 0 | [5 empty] | 674490 | 0
|  | 95 | 0 | 95 | 0 | 95 | 0 | 95 | 0 | 95 | 0 |  |  |  |  | 1500-2000mm | 0 | [11 empty] | 730616 | 0
|  | 120 | 0 | 120 | 0 | 120 | 0 | 120 | 0 | 120 | 0 | [10 empty] | Earth Strip Qty (LA ) | [6 empty] | 787507 | 0
|  | 150 | 0 | 150 | 0 | 150 | 0 | 150 | 0 | 150 | 0 | [10 empty] | 25x3mm | 0 | [5 empty] | 843332 | 0
|  | 185 | 0 | 185 | 0 | 185 | 0 | 185 | 0 | 185 | 0 | [10 empty] | 25x6mm | 120 | [5 empty] | 899400 | 0
|  | 240 | 0 | 240 | 0 | 240 | 0 | 240 | 0 | 240 | 0 |  |  |  | AC Cable tray total Qty(INV TO ACCB) | [6 empty] | 40x6mm | 0 | [5 empty] | 938113 | 0
|  | 300 | 0 | 300 | 0 | 300 | 0 | 300 | 0 | 300 | 0 |  |  |  | 100x75x2mm |  | 20 |  |  |  |  | 50x6mm | 0 | [5 empty] | 993611 | 0
|  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  |  | 150x75x2mm |  | 0 | [11 empty] | 1048969 | 0
|  | 16 | 0 | 16 | 0 | 16 | 0 | 16 | 0 | 16 | 0 |  |  |  | 200x75x2mm |  | 0 | [11 empty] | 1073832 | 0
|  | 25 | 0 | 25 | 0 | 25 | 0 | 25 | 0 | 25 | 0 |  |  |  | 300x75x2mm |  | 0 | [11 empty] | 1128068 | 0
|  | 35 | 0 | 35 | 0 | 35 | 0 | 35 | 0 | 35 | 0 |  |  |  | 400x75x2mm |  | 0 | [11 empty] | 1181833 | 0
|  | 50 | 0 | 50 | 0 | 50 | 0 | 50 | 0 | 50 | 0 |  |  |  | 500x75x2mm |  | 0 | [11 empty] | 1200844 | 0
|  | 70 | 0 | 70 | 0 | 70 | 0 | 70 | 0 | 70 | 0 |  |  |  | 600x75x2mm |  | 0 | [11 empty] | 1242041 | 0
|  | 95 | 0 | 95 | 0 | 95 | 0 | 95 | 0 | 95 | 0 |  |  |  | Soil Trench |  | 0 | [11 empty] | 1304160 | 0
|  | 120 | 0 | 120 | 0 | 120 | 0 | 120 | 0 | 120 | 0 | [17 empty] | 1346116 | 0
|  | 150 | 0 | 150 | 0 | 150 | 0 | 150 | 0 | 150 | 0 | [10 empty] | DC/AC Cable tray & Earth strip Total Qty | [6 empty] | 1397881 | 0
|  | 185 | 0 | 185 | 0 | 185 | 0 | 185 | 0 | 185 | 0 | [10 empty] | 100x75x2mm |  | 190 | 25x3mm | 1024 |  |  | 1450824 | 0
|  | 240 | 0 | 240 | 0 | 240 | 0 | 240 | 0 | 240 | 0 |  |  |  | AC Cable tray total Qty(ACCB TO CLTP) | [6 empty] | 150x75x2mm |  | 0 | 25x6mm | 120 |  |  | 1491179 | 0
|  | 300 | 0 | 300 | 0 | 300 | 0 | 300 | 0 | 300 | 0 |  |  |  | 100x75x2mm |  | 170 |  |  |  |  | 200x75x2mm |  | 220 | 40x6mm | 0 |  |  | 1544169 | 0
|  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  |  | 150x75x2mm |  | 0 |  |  |  |  | 300x75x2mm |  | 0 | 50x6mm | 0 |  |  | 1624169 | 0
|  | 16 | 0 | 16 | 0 | 16 | 0 | 16 | 0 | 16 | 0 |  |  |  | 200x75x2mm |  | 220 |  |  |  |  | 400x75x2mm |  | 0 | 4 Sqmm | 0 |  |  | Total | 344336
|  | 25 | 0 | 25 | 0 | 25 | 0 | 25 | 0 | 25 | 0 |  |  |  | 300x75x2mm |  | 0 |  |  |  |  | 500x75x2mm |  | 0 | 6 Sqmm | 0 |  |  | per watt Cost | 0
|  | 35 | 0 | 35 | 0 | 35 | 0 | 35 | 0 | 35 | 0 |  |  |  | 400x75x2mm |  | 0 |  |  |  |  | 600x75x2mm |  | 0 | 50X50x2mm | 350
|  | 50 | 0 | 50 | 0 | 50 | 0 | 50 | 0 | 50 | 0 |  |  |  | 500x75x2mm |  | 0 |  |  |  |  | Soil trench (INV to ACCB) |  | 0
|  | 70 | 0 | 70 | 0 | 70 | 0 | 70 | 0 | 70 | 0 |  |  |  | 600x75x2mm |  | 0 |  |  |  |  | Soil trench (ACCB to CLTP) |  | 0
|  | 95 | 0 | 95 | 0 | 95 | 0 | 95 | 0 | 95 | 0 |  |  |  | Soil Trench |  | 0
|  | 120 | 0 | 120 | 0 | 120 | 0 | 120 | 0 | 120 | 0
|  | 150 | 0 | 150 | 0 | 150 | 0 | 150 | 0 | 150 | 0 | [14 empty] | Net Metering/Net Billing
|  | 185 | 0 | 185 | 0 | 185 | 0 | 185 | 0 | 185 | 0 | [12 empty] | Origin | Cost
|  | 240 | 0 | 240 | 0 | 240 | 0 | 240 | 0 | 240 | 0 |  |  | Cable length (INV to LT panel) |  |  |  | Cable length (ACCB to CLTP) | [5 empty] | Indian ALMM | 16
|  | 300 | 0 | 300 | 0 | 300 | 0 | 300 | 0 | 300 | 0 |  |  | Count of selection | Size (sqmm) | Length (Mtrs) |  | Size (sqmm) |  |  | Length (Mtrs) | No. or Run |  | Indian ALCM | 22
|  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | 4CX16Sqmm | 0 |  | 3.5CX16Sqmm |  |  | 0 | 0 |  | Imported | 15
|  | 16 | 0 | 16 | 0 | 16 | 0 | 16 | 0 | 16 | 0 |  |  | 0 | 3.5CX25Sqmm | 0 |  | 3.5CX25Sqmm |  |  | 0 | 0
|  | 25 | 0 | 25 | 0 | 25 | 0 | 25 | 0 | 25 | 0 |  |  | 0 | 3.5CX35Sqmm | 0 |  | 3.5CX35Sqmm |  |  | 0 | 0
|  | 35 | 0 | 35 | 0 | 35 | 0 | 35 | 0 | 35 | 0 |  |  | 0 | 3.5CX50Sqmm | 0 |  | 3.5CX50Sqmm |  |  | 0 | 0
|  | 50 | 0 | 50 | 0 | 50 | 0 | 50 | 0 | 50 | 0 |  |  | 0 | 3.5CX70Sqmm | 0 |  | 3.5CX70Sqmm |  |  | 0 | 0
|  | 70 | 0 | 70 | 0 | 70 | 0 | 70 | 0 | 70 | 0 |  |  | 0 | 3.5CX95Sqmm | 0 |  | 3.5CX95Sqmm |  |  | 0 | 0
|  | 95 | 0 | 95 | 0 | 95 | 0 | 95 | 0 | 95 | 0 |  |  | 0 | 3.5CX120Sqmm | 0 |  | 3.5CX120Sqmm |  |  | 0 | 0
|  | 120 | 0 | 120 | 0 | 120 | 0 | 120 | 0 | 120 | 0 |  |  | 0 | 3.5CX150Sqmm | 0 |  | 3.5CX150Sqmm |  |  | 0 | 0
|  | 150 | 0 | 150 | 0 | 150 | 0 | 150 | 0 | 150 | 0 |  |  | 0 | 3.5CX185Sqmm | 0 |  | 3.5CX185Sqmm |  |  | 440 | 2
|  | 185 | 0 | 185 | 0 | 185 | 0 | 185 | 0 | 185 | 0 |  |  | 0 | 3.5CX240Sqmm | 0 |  | 3.5CX240Sqmm |  |  | 0 | 0
|  | 240 | 0 | 240 | 0 | 240 | 0 | 240 | 0 | 240 | 0 |  |  | 2 | 3.5CX300Sqmm | 20 |  | 3.5CX300Sqmm |  |  | 170 | 1
|  | 300 | 0 | 300 | 0 | 300 | 0 | 300 | 0 | 300 | 0 |  |  | 2 |  | 20
|  | 0 |  | 0 |  | 0 |  | 0 |  | 0
|  | 16 | 0 | 16 | 0 | 16 | 0 | 16 | 0 | 16 | 0 | [6 empty] | DC cable break up
|  | 25 | 0 | 25 | 0 | 25 | 0 | 25 | 0 | 25 | 0 | [6 empty] | 4 Sqmm possitive |  |  | 2025
|  | 35 | 0 | 35 | 0 | 35 | 0 | 35 | 0 | 35 | 0 |  |  | 10 |  |  |  | 4 Sqmm negative |  |  | 2025
|  | 50 | 0 | 50 | 0 | 50 | 0 | 50 | 0 | 50 | 0 | [6 empty] | 6 Sqmm possitive |  |  | 0
|  | 70 | 0 | 70 | 0 | 70 | 0 | 70 | 0 | 70 | 0 | [6 empty] | 4 Sqmm negative |  |  | 0
|  | 95 | 0 | 95 | 0 | 95 | 0 | 95 | 0 | 95 | 0
|  | 120 | 0 | 120 | 0 | 120 | 0 | 120 | 0 | 120 | 0
|  | 150 | 0 | 150 | 0 | 150 | 0 | 150 | 0 | 150 | 0
|  | 185 | 0 | 185 | 0 | 185 | 0 | 185 | 0 | 185 | 0
|  | 240 | 0 | 240 | 0 | 240 | 0 | 240 | 0 | 240 | 0 |  |  |  | Monkey | 0
|  | 300 | 0 | 300 | 0 | 300 | 0 | 300 | 0 | 300 | 0 |  |  |  | Staircase | 0
|  | ACCB to CLTP | [12 empty] | Movable | 0
|  | 16 | 0
|  | 25 | 0 |  | Base 24 mm - ECO 70 | [9 empty] | Lightning Arrester Summary
|  | 35 | 0 |  | Trapezoidal |  |  | Type of installation |  | Count of selection |  |  |  |  | Type | Qty.
|  | 50 | 0 |  | Land scape - 250 MM |  |  | Shed |  | 0
|  | 70 | 0 |  | Land scape - 300 MM |  |  | Long Rail |  | 0 |  |  |  |  | ESE 107 Mtrs Radius | 1
|  | 95 | 0 |  | Standing seam |  |  | RCC |  | 0 |  |  |  |  | Air Ligthing Terminal | 0
|  | 120 | 0 |  | Kliplock |  |  | RCC Raised |  | 1
|  | 150 | 0 |  | SSB6 Profiles-120MM |  |  | RCC Raised on Pillars |  | 0
|  | 185 | 440 |  | SSB2 Profiles-50MM |  |  | Ground Mounted |  | 0
|  | 240 | 0 |  | RCC & RCC raised |  |  | Parking- Car/Bike |  | 0
|  | 300 | 170 |  | Ground & Parking |  |  | Parking-Truck/Bus |  | 0
[8 empty] | Floating |  | 0
[8 empty] | Total Qty |  | 1
|  |  | CEIG, NET Metering & Approvals Summary Sheet | [7 empty] | 1
|  |  | State Name |  | Maharashtra
|  |  | Total Capcity (String Inverter LT) (DC & AC) |  | 400.52 | 300
|  |  | Exisiting Plant capacity in Kwp |  | 0 | 0
|  |  | Approvals |  | Price | per Wp
|  |  | CEIG for new plant |  | 190000 | 0.47438
|  |  | NET metering Liaisoning fee NOC |  | 290000 | 0.72406
|  |  | NET metering material & Installation |  | 200000 | 0.49935
|  |  | Cubicle |  | 300000 | 0.74903
|  |  | Statutory |  | 40000 | 0.09987
|  |  | RPO |  | 0 | 0
|  |  |  | Net Metering |  |  |  |  | CEIG | Total | Grand Total | Per Wp | HT CT/PT Installation |  |  |  | Renewable Purchase Obligation
|  |  |  | A | B | C | Statutory | D=B+C | E | F=A+E | G=D+E | L=F/wp | M | N | O=M+N | M= G+O
| Sr.No | State | Capacity | NET metering Liaisoning fee (Discom NOC) | Material | Installation | Statutory Application Fee for NET Meter/CEIG Nodal Agency _Material testing fee | Total cost of NET Metering inst. work | CEIG liasoning | NET Metering and CEIG liaisoning | Total cost of NET Metering work and CEIG liaisoning | P/Wp | Rate for one HT Kiosk(voltage level-11kV,22kV &33kV) *Earthing and othe installation work not included | Installtion/testing laisoning/Statutory | Total | NET Metering and CEIG liaisoning Including HT and LT Material Cost-Cost For Single Qty | RPO (1. Project Approval from Nodaloffice/State Energy Development Agency 2.Grid Connectivity & Metering approval from SEDCL 3.Solar Plant Commissioning Approval from SEDCL HO
| 1 | Madhya Pradesh | 25-100 KWp | 125000 | 80000 | 15000 | 40000 | 95000 | 0 | 125000 | 95000 | 1.9 | 550000 | 100000 | 650000 | 745000
|  |  | 101-250 KWp | 150000 | 100000 | 30000 | 40000 | 130000 | 150000 | 300000 | 280000 | 2.8 | 550000 | 100000 | 650000 | 930000
|  |  | 251-500 KWp | 200000 | 100000 | 30000 | 100000 | 130000 | 250000 | 450000 | 380000 | 0.76 | 550000 | 100000 | 650000 | 1030000
|  |  | 501- 1000 KWp | 500000 | 100000 | 50000 | 300000 | 150000 | 350000 | 850000 | 500000 | 0.5 | 550000 | 100000 | 650000 | 1150000 | 400000 | Satutaryfee
|  | Gujarat | 1 kWp-50 KW | 50000 | 150000 | 10000 | 50000 | 160000 | 100000 | 150000 | 260000 | 5.2 | 225000 | 100000 | 325000 | 585000 | 0 | 84000
| 2 |  | 100-200 KW | 150000 | 200000 | 15000 | 50000 | 215000 | 150000 | 300000 | 365000 | 3.65 | 350000 | 100000 | 450000 | 815000 |  | 333750
|  |  | 201-500 KW | 200000 | 250000 | 20000 | 50000 | 270000 | 300000 | 500000 | 570000 | 1.14 | 350000 | 100000 | 450000 | 1020000 | 350000 | 834375
|  |  | 501-1000 KW | 300000 | 300000 | 30000 | 50000 | 330000 | 450000 | 750000 | 780000 | 0.78 | 350000 | 100000 | 450000 | 1230000 | 450000 | 1668750
| 3 | Maharashtra | Upto 200 KW | 230000 | 180000 | 20000 | 40000 | 200000 | 150000 | 380000 | 350000 | 7 | 200000 | 100000 | 300000 | 650000 | 0
|  |  | 200 to 500 KW | 290000 | 180000 | 20000 | 40000 | 200000 | 190000 | 480000 | 390000 | 3.9 | 200000 | 100000 | 300000 | 690000 | 0
|  |  | 500 to 750 KW | 340000 | 260000 | 40000 | 40000 | 300000 | 250000 | 590000 | 550000 | 1.1 | 200000 | 100000 | 300000 | 850000 | 0
|  |  | 750 to 1000 KW | 400000 | 260000 | 40000 | 40000 | 300000 | 390000 | 790000 | 690000 | 0.69 | 200000 | 100000 | 300000 | 990000 | 0
|  |  | 1000 to 2000 KW | 430000 | 350000 | 30000 | 50000 | 380000 | 390000 | 820000 | 770000 | 0.77 | 200000 | 100000 | 300000 | 1070000 | 0
| 4 | Bihar | 1 kWp-50 KW | 60000 | 50000 | 10000 | 30000 | 60000 | 50000 | 110000 | 110000 | 2.2 | 225000 | 100000 | 325000 | 435000 | 0
|  |  | 51 kWp-100 KW | 80000 | 64000 | 25000 | 30000 | 89000 | 80000 | 160000 | 169000 | 1.69 | 225000 | 100000 | 325000 | 494000 | 0
|  |  | 101 kWp-500 KW | 100000 | 68000 | 30000 | 30000 | 98000 | 100000 | 200000 | 198000 | 0.396 | 225000 | 100000 | 325000 | 523000 | 280000
|  |  | 501 kWp-1000 KW | 150000 | 75000 | 35000 | 30000 | 110000 | 150000 | 300000 | 260000 | 0.26 | 225000 | 100000 | 325000 | 585000 | 350000
| 5 | Jharkhand | 1 kWp-50 KWp | 50000 | 64000 | 10000 | 30000 | 74000 | 50000 | 100000 | 124000 | 2.48 | 225000 | 100000 | 325000 | 449000 | 0
|  |  | 51 kWp-100 KWp | 50000 | 64000 | 25000 | 30000 | 89000 | 50000 | 100000 | 139000 | 1.39 | 225000 | 100000 | 325000 | 464000 | 0
|  |  | 101 kWp-500 KWp | 100000 | 68000 | 30000 | 30000 | 98000 | 110000 | 210000 | 208000 | 0.416 | 225000 | 100000 | 325000 | 533000 | 280000
|  |  | 501 kWp-1000 KWp | 100000 | 75000 | 35000 | 30000 | 110000 | 150000 | 250000 | 260000 | 0.26 | 225000 | 100000 | 325000 | 585000 | 350000
| 6 | Goa | 1 kWp-50 KWp | 60000 | 100000 | 10000 | 30000 | 110000 | 50000 | 110000 | 160000 | 3.2 | 225000 | 100000 | 325000 | 485000 | 0
|  |  | 51 kWp-100 KWp | 100000 | 150000 | 25000 | 30000 | 175000 | 60000 | 160000 | 235000 | 2.35 | 225000 | 100000 | 325000 | 560000 | 0
|  |  | 101 kWp-500 KWp | 140000 | 200000 | 30000 | 30000 | 230000 | 150000 | 290000 | 380000 | 0.76 | 225000 | 100000 | 325000 | 705000 | 300000
|  |  | 501 kWp-1000 KWp | 200000 | 250000 | 35000 | 30000 | 285000 | 200000 | 400000 | 485000 | 0.485 | 225000 | 100000 | 325000 | 810000 | 380000
| 7 | Odisha | 1 kWp-50 KWp | 75000 | 70000 | 15000 | 20000 | 85000 | 50000 | 125000 | 135000 | 2.7 | 225000 | 100000 | 325000 | 460000 | 0
|  |  | 51 kWp-100 KWp | 100000 | 70000 | 20000 | 20000 | 90000 | 50000 | 150000 | 140000 | 1.4 | 225000 | 100000 | 325000 | 465000 | 0
|  |  | 101 kWp-500 KWp | 150000 | 70000 | 25000 | 30000 | 95000 | 90000 | 240000 | 185000 | 0.37 | 225000 | 100000 | 325000 | 510000 | 200000
|  |  | 501 kWp-1000 KWp | 210000 | 70000 | 25000 | 30000 | 95000 | 115000 | 325000 | 210000 | 0.21 | 225000 | 100000 | 325000 | 535000 | 300000
| 8 | Uttar Pradesh | 1 kWp-50 KWp | 80000 | 90000 | 10000 | 20000 | 100000 | 70000 | 150000 | 170000 | 3.4 | 225000 | 100000 | 325000 | 495000 | 0
|  |  | 51 kWp-100 KWp | 150000 | 100000 | 20000 | 30000 | 120000 | 130000 | 280000 | 250000 | 2.5 | 225000 | 100000 | 325000 | 575000 | 0
|  |  | 101 kWp-500 KWp | 150000 | 100000 | 20000 | 50000 | 120000 | 200000 | 350000 | 320000 | 0.64 | 225000 | 100000 | 325000 | 645000 | 300000
|  |  | 501 kWp-1000 KWp | 180000 | 150000 | 30000 | 100000 | 180000 | 225000 | 405000 | 405000 | 0.405 | 225000 | 100000 | 325000 | 730000 | 400000
| 9 | Delhi | 1 kWp-50 KWp | 50000 | 60000 | 10000 | 30000 | 70000 | 50000 | 100000 | 120000 | 2.4 | 225000 | 100000 | 325000 | 445000 | 0
|  |  | 51 kWp-100 KWp | 65000 | 94000 | 30000 | 30000 | 124000 | 80000 | 145000 | 204000 | 2.04 | 225000 | 100000 | 325000 | 529000 | 0
|  |  | 101 kWp-500 KWp | 120000 | 98000 | 35000 | 30000 | 133000 | 180000 | 300000 | 313000 | 0.626 | 225000 | 100000 | 325000 | 638000 | 350000
|  |  | 501 kWp-1000 KWp | 120000 | 105000 | 40000 | 30000 | 145000 | 280000 | 400000 | 425000 | 0.425 | 225000 | 100000 | 325000 | 750000 | 420000
| 10 | Haryana | 1 kWp-50 KWp | 50000 | 94000 | 15000 | 30000 | 109000 | 50000 | 100000 | 159000 | 3.18 | 225000 | 100000 | 325000 | 484000 | 0
|  |  | 51 kWp-100 KWp | 70000 | 94000 | 30000 | 30000 | 124000 | 60000 | 130000 | 184000 | 1.84 | 225000 | 100000 | 325000 | 509000 | 0
|  |  | 101 kWp-500 KWp | 125000 | 125000 | 35000 | 30000 | 160000 | 150000 | 275000 | 310000 | 0.62 | 225000 | 100000 | 325000 | 635000 | 280000
|  |  | 501 kWp-1000 KWp | 150000 | 150000 | 35000 | 30000 | 185000 | 200000 | 350000 | 385000 | 0.385 | 0 | 0 | 0 | 385000 | 0
| 11 | Tamil Nadu | 1 kW-50 KW | 100000 | 170000 | 30000 | 50000 | 200000 | 172500 | 272500 | 372500 | 7.45 | 225000 | 100000 | 325000 | 697500 | 0
|  |  | 51 kW-100 KW | 200000 | 170000 | 30000 | 50000 | 200000 | 395000 | 595000 | 595000 | 5.95 | 225000 | 100000 | 325000 | 920000 | 0
|  |  | 101 kW-500 KW | 250000 | 170000 | 30000 | 50000 | 200000 | 1300000 | 1550000 | 1500000 | 3 | 225000 | 100000 | 325000 | 1825000 | 0
|  |  | 501 kW-1000 KW | 250000 | 170000 | 40000 | 50000 | 210000 | 2350000 | 2600000 | 2560000 | 2.56 | 225000 | 100000 | 325000 | 2885000 | 0
|  |  | above 1000 KW | 0 | 0 | 0 | 0 | 0 | 780000 | 780000 | 780000 | 0.78 | 225000 | 100000 | 325000 | 1105000 | 0
| 12 | Punjab | 1 kWp-50 KWp | 70000 | 94000 | 10000 | 30000 | 104000 | 60000 | 130000 | 164000 | 3.28 | 225000 | 100000 | 325000 | 489000 | 0
|  |  | 51 kWp-100 KWp | 70000 | 94000 | 30000 | 30000 | 124000 | 70000 | 140000 | 194000 | 1.94 | 225000 | 100000 | 325000 | 519000 | 0
|  |  | 101 kWp-500 KWp | 125000 | 110000 | 35000 | 30000 | 145000 | 150000 | 275000 | 295000 | 0.59 | 225000 | 100000 | 325000 | 620000 | 280000
|  |  | 501 kWp-1000 KWp | 150000 | 150000 | 35000 | 30000 | 185000 | 200000 | 350000 | 385000 | 0.385 | 0 | 0 | 0 | 385000 | 0
| 13 | Himachal Pradesh | 1 kWp-50 KW | 50000 | 94000 | 10000 | 30000 | 104000 | 60000 | 110000 | 164000 | 3.28 | 225000 | 100000 | 325000 | 489000 | 0
|  |  | 51 kWp-100 KW | 50000 | 94000 | 20000 | 30000 | 114000 | 80000 | 130000 | 194000 | 1.94 | 225000 | 100000 | 325000 | 519000 | 0
|  |  | 101 kWp-500 KW | 150000 | 98000 | 30000 | 30000 | 128000 | 180000 | 330000 | 308000 | 0.616 | 225000 | 100000 | 325000 | 633000 | 300000
|  |  | 501 kWp-1000 KW | 200000 | 105000 | 40000 | 30000 | 145000 | 200000 | 400000 | 345000 | 0.345 | 225000 | 100000 | 325000 | 670000 | 380000
| 14 | Rajasthan | 1 kWp-50 KWp | 80000 | 75000 | 10000 | 20000 | 85000 | 60000 | 140000 | 145000 | 2.9 | 275000 | 100000 | 375000 | 520000 | 0
|  |  | 51 kWp-100 KWp | 90000 | 75000 | 20000 | 30000 | 95000 | 80000 | 170000 | 175000 | 1.75 | 275000 | 100000 | 375000 | 550000 | 0
|  |  | 101 kWp-500 KWp | 140000 | 115000 | 20000 | 30000 | 135000 | 160000 | 300000 | 295000 | 0.59 | 275000 | 100000 | 375000 | 670000 | 300000
|  |  | 501 kWp-1000 KWp | 200000 | 120000 | 20000 | 30000 | 140000 | 200000 | 400000 | 340000 | 0.34 | 0 | 0 | 0 | 340000 | 0
| 15 | Telangana | 1 kWp-50 KWp | 75000 | 45000 | 15000 | 30000 | 60000 | 75000 | 150000 | 135000 | 3 | 225000 | 100000 | 325000 | 460000 | 0
|  |  | 51 kWp-100 KWp | 100000 | 55000 | 20000 | 30000 | 75000 | 85000 | 185000 | 160000 | 1.85 | 225000 | 100000 | 325000 | 485000 | 0
|  |  | 101 kWp-500 KWp | 200000 | 80000 | 25000 | 30000 | 105000 | 185000 | 385000 | 290000 | 0.77 | 250000 | 100000 | 350000 | 640000 | 280000
|  |  | 501 kWp-1000 KWp | 250000 | 80000 | 25000 | 30000 | 105000 | 200000 | 450000 | 305000 | 0.45 | 250000 | 100000 | 350000 | 655000 | 350000
| 16 | West Bengal | 1 kWp-50 KWp | 60000 | 64000 | 30000 | 30000 | 94000 | 60000 | 120000 | 154000 | 3.08 | 225000 | 100000 | 325000 | 479000 | 0
|  |  | 51 kWp-100 KWp | 80000 | 64000 | 30000 | 30000 | 94000 | 80000 | 160000 | 174000 | 1.74 | 225000 | 100000 | 325000 | 499000 | 0
|  |  | 101 kWp-500 KWp | 100000 | 68000 | 40000 | 30000 | 108000 | 100000 | 200000 | 208000 | 0.416 | 225000 | 100000 | 325000 | 533000 | 280000
|  |  | 501 kWp-1000 KWp | 170000 | 75000 | 40000 | 30000 | 115000 | 170000 | 340000 | 285000 | 0.285 | 225000 | 100000 | 325000 | 610000 | 350000
| 17 | Karnataka | 1 kWp-50 KWp | 520676 | 100000 | 50000 | 45000 | 150000 | 600780 | 1121456 | 750780 | 15.0156 | 125000 | 100000 | 225000 | 975780 | 0
|  |  | 51 kWp-100 KWp | 520676 | 100000 | 50000 | 45000 | 150000 | 600780 | 1121456 | 750780 | 7.5078 | 125000 | 100000 | 225000 | 975780 | 0
|  |  | 101 kWp-500 KWp | 520676 | 100000 | 50000 | 100000 | 150000 | 600780 | 1121456 | 750780 | 1.5016 | 125000 | 100000 | 225000 | 975780 | 0 |  |  |  | NOC | CEIG
,\ |  |  | 501 kWp-1000 KWp | 400520 | 100000 | 50000 | 100000 | 150000 | 600780 | 1001300 | 750780 | 0.75078 | 125000 | 100000 | 225000 | 975780 | 0 | more then 1MWp
| 18 | Andhra Pradesh | 1 kWp-50 KWp | 75000 | 180000 | 15000 | 20000 | 195000 | 75000 | 150000 | 270000 | 3 | 225000 | 100000 | 325000 | 595000 | 0
|  |  | 51 kWp-100 KWp | 100000 | 180000 | 20000 | 20000 | 200000 | 85000 | 185000 | 285000 | 1.85 | 225000 | 100000 | 325000 | 610000 | 0
|  |  | 101 kWp-500 KWp | 200000 | 200000 | 25000 | 30000 | 225000 | 185000 | 385000 | 410000 | 0.77 | 250000 | 100000 | 350000 | 760000 | 280000
|  |  | 501 kWp-1000 KWp | 250000 | 200000 | 25000 | 30000 | 225000 | 200000 | 450000 | 425000 | 0.45 | 250000 | 100000 | 350000 | 775000 | 350000
| 19 | Kerala | 1 kWp-50 KW | 100000 | 100000 | 30000 | 30000 | 130000 | 100000 | 200000 | 230000 | 4.6 | 225000 | 100000 | 325000 | 555000 | 0
|  |  | 51 kWp-100 KW | 150000 | 100000 | 30000 | 30000 | 130000 | 175000 | 325000 | 305000 | 3.05 | 225000 | 100000 | 325000 | 630000 | 0
|  |  | 101 kWp-500 KW | 250000 | 100000 | 40000 | 30000 | 140000 | 275000 | 525000 | 415000 | 0.83 | 225000 | 100000 | 325000 | 740000 | 0
|  |  | 501 kWp-1000 KW | 350000 | 100000 | 40000 | 30000 | 140000 | 400000 | 750000 | 540000 | 0.54 | 225000 | 100000 | 325000 | 865000 | 0
| 20 | Chhattisgarh | 1 kWp-50 KWp | 70000 | 94000 | 25000 | 30000 | 119000 | 60000 | 130000 | 179000 | 3.58 | 225000 | 100000 | 325000 | 504000 | 0
|  |  | 51 kWp-100 KWp | 100000 | 94000 | 20000 | 30000 | 114000 | 70000 | 170000 | 184000 | 1.84 | 225000 | 100000 | 325000 | 509000 | 0
|  |  | 101 kWp-500 KWp | 150000 | 98000 | 20000 | 30000 | 118000 | 150000 | 300000 | 268000 | 0.536 | 225000 | 100000 | 325000 | 593000 | 300000
|  |  | 501 kWp-1000 KWp | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 21 | Uttarakhand | 1 kWp-50 KWp | 80000 | 94000 | 20000 | 30000 | 114000 | 70000 | 150000 | 184000 | 3.68 | 225000 | 100000 | 325000 | 509000 | 0
|  |  | 51 kWp-100 KWp | 90000 | 94000 | 20000 | 30000 | 114000 | 80000 | 170000 | 194000 | 1.94 | 225000 | 100000 | 325000 | 519000 | 0
|  |  | 101 kWp-500 KWp | 150000 | 110000 | 30000 | 30000 | 140000 | 100000 | 250000 | 240000 | 0.48 | 225000 | 100000 | 325000 | 565000 | 280000
|  |  | 501 kWp-1000 KWp | 200000 | 125000 | 40000 | 30000 | 165000 | 150000 | 350000 | 315000 | 0.315 | 225000 | 100000 | 325000 | 640000 | 350000
| 22 | Daman & Diu | 1 kWp-50 KWp | 50000 | 50000 | 10000 | 30000 | 60000 | 50000 | 100000 | 110000 | 2.2 | 225000 | 100000 | 325000 | 435000 | 0
|  |  | 51 kWp-100 KWp | 50000 | 94000 | 20000 | 30000 | 114000 | 50000 | 100000 | 164000 | 1.64 | 225000 | 100000 | 325000 | 489000 | 0
|  |  | 101 kWp-500 KWp | 175000 | 98000 | 30000 | 30000 | 128000 | 200000 | 375000 | 328000 | 0.656 | 225000 | 100000 | 325000 | 653000 | 300000
|  |  | 501 kWp-1000 KWp | 200000 | 105000 | 40000 | 30000 | 145000 | 300000 | 500000 | 445000 | 0.445 | 225000 | 100000 | 325000 | 770000 | 400000
| 23 | Jammu and Kashmir | 1 kWp-50 KWp | 100000 | 94000 | 20000 | 30000 | 114000 | 80000 | 180000 | 194000 | 3.88 | 225000 | 100000 | 325000 | 519000 | 0
|  |  | 51 kWp-100 KWp | 100000 | 94000 | 20000 | 30000 | 114000 | 80000 | 180000 | 194000 | 1.94 | 225000 | 100000 | 325000 | 519000 | 0
|  |  | 101 kWp-500 KWp | 150000 | 98000 | 30000 | 30000 | 128000 | 150000 | 300000 | 278000 | 0.556 | 225000 | 100000 | 325000 | 603000 | 300000
|  |  | 501 kWp-1000 KWp | 200000 | 105000 | 40000 | 30000 | 145000 | 200000 | 400000 | 345000 | 0.345 | 225000 | 100000 | 325000 | 670000 | 400000
| 24 | Meghalaya | 1 kWp-50 KWp | 100000 | 94000 | 20000 | 30000 | 114000 | 100000 | 200000 | 214000 | 4.28 | 225000 | 100000 | 325000 | 539000 | 0
|  |  | 51 kWp-100 KWp | 100000 | 94000 | 20000 | 30000 | 114000 | 100000 | 200000 | 214000 | 2.14 | 225000 | 100000 | 325000 | 539000 | 0
|  |  | 101 kWp-500 KWp | 180000 | 98000 | 30000 | 30000 | 128000 | 150000 | 330000 | 278000 | 0.556 | 225000 | 100000 | 325000 | 603000 | 300000
|  |  | 501 kWp-1000 KWp | 250000 | 105000 | 40000 | 30000 | 145000 | 300000 | 550000 | 445000 | 0.445 | 225000 | 100000 | 325000 | 770000 | 380000
| 25 | Assam | 1 kWp-50 KWp | 100000 | 94000 | 10000 | 30000 | 104000 | 100000 | 200000 | 204000 | 4.08 | 225000 | 100000 | 325000 | 529000 | 0
|  |  | 51 kWp-100 KWp | 100000 | 94000 | 20000 | 30000 | 114000 | 100000 | 200000 | 214000 | 2.14 | 225000 | 100000 | 325000 | 539000 | 0
|  |  | 101 kWp-500 KWp | 180000 | 98000 | 30000 | 30000 | 128000 | 150000 | 330000 | 278000 | 0.556 | 225000 | 100000 | 325000 | 603000 | 300000
|  |  | 501 kWp-1000 KWp | 250000 | 105000 | 40000 | 30000 | 145000 | 300000 | 550000 | 445000 | 0.445 | 225000 | 100000 | 325000 | 770000 | 380000
| 26 | Dadra & Nagar Haveli | 1 kWp-50 KWp | 50000 | 94000 | 10000 | 30000 | 104000 | 50000 | 100000 | 154000 | 3.08 | 225000 | 100000 | 325000 | 479000 | 0
|  |  | 51 kWp-100 KWp | 50000 | 94000 | 20000 | 30000 | 114000 | 50000 | 100000 | 164000 | 1.64 | 225000 | 100000 | 325000 | 489000 | 0
|  |  | 101 kWp-500 KWp | 175000 | 98000 | 30000 | 30000 | 128000 | 200000 | 375000 | 328000 | 0.656 | 225000 | 100000 | 325000 | 653000 | 300000
|  |  | 501 kWp-1000 KWp | 200000 | 105000 | 40000 | 30000 | 145000 | 300000 | 500000 | 445000 | 0.445 | 225000 | 100000 | 325000 | 770000 | 380000
Andhra Pradesh
| Arunachal Pradesh |  | Earthing Calculation | [7 empty] | Generation Panel before client termination
| Assam |  | LT Panel capacity | No. of earthing | Total earthing |  | FRP |  |  |  | Rating | Panel price | Total price
| Bihar |  | 10-50kw | 3 | 0 |  | GI |  |  |  | 100A | 50347 | 0
| Chhattisgarh |  | 50-100kw | 5 | 10 |  | HDG |  |  |  | 200A | 60484 | 120968
| Goa |  | 150-499kw | 6 | 0 |  | Soil Trench |  |  |  | 400A | 80484 | 0
| Gujarat |  | 500-999kw | 12 | 0 | [5 empty] | 500A | 100000 | 0
| Haryana |  | 1000-1500kw | 18 | 0 | [5 empty] | 630A | 110000 | 0
| Himachal Pradesh |  | Total no of earthing |  | 10 | [5 empty] | 800A | 125000 | 0
| Jammu and Kashmir | [9 empty] | 1000A | 200000 | 0
| Jharkhand | [9 empty] | 1200A | 235000 | 0
| Karnataka |  | RPR /UVR/NVR | [7 empty] | 1600A | 275000 | 0
| Kerala |  | S.No | Rating(Amps) | Material price | Enclosure price | Total Price | Total cost |  |  | 2000A | 320000 | 0
| Madhya Pradesh |  | 1 | 100 | 10469 | 7161 | 17630 | 0 |  |  |  |  | 120968
| Maharashtra |  | 2 | 125 | 11385 | 7161 | 18546 | 37092
| Manipur |  | 3 | 200 | 26635 | 10075 | 36710 | 0
| Meghalaya |  | 4 | 250 | 30965 | 10075 | 41040 | 0
| Mizoram |  | 5 | 320 | 43775 | 14102 | 57877 | 0
| Nagaland |  | 6 | 400 | 55578 | 15659 | 71237 | 0 |  |  | Earthing Calculation
| Odisha |  | 7 | 500 | 68721 | 15659 | 84380 | 0 |  |  | LT Panel capacity | No. of earthing | Total earthing
| Punjab |  | 8 | 630/700 | 99032 | 21816 | 120848 | 0 |  |  | 10-50kw | 3 | 0
| Rajasthan |  | 9 | 800/1000 upto 4000A | 140414 | 33657 | 174071 | 0 |  |  | 50-100kw | 5 | 10
| Sikkim | [6 empty] | 37092 |  |  | 150-499kw | 6 | 0
| Tamil Nadu | [9 empty] | 500-999kw | 12 | 0
| Telangana | [9 empty] | 1000-1500kw | 18 | 0
| Tripura | [9 empty] | Total no of earthing |  | 13
| Uttar Pradesh |  |  | Spare feeder calculation
| Uttarakhand |  | Breaker type | Rating | Price for breaker | Price for BB | Total price | Total price |  | Conductor/ ACCB Panel for AP
| West Bengal |  | MCCB | 100 | 11160 | 48000 | 59160 | 0 |  | Breaker type | S.No | Rating(Amps) | Panel Price | Panel Price
| Daman & Diu |  |  | 200 | 21000 | 66000 | 87000 | 174000 |  | MCCB | 1 | 200 | 37000 | 74000
| Pondicherry |  |  | 320 | 31800 | 72000 | 103800 | 207600 |  |  | 2 | 255 | 42000 | 0
| Dadra & Nagar Haveli |  |  | 400 | 34200 | 80500 | 114700 | 0 |  |  | 3 | 235 | 60000 | 0
| Delhi |  |  | 500 | 35400 | 103500 | 138900 | 0 |  |  | 4 | 400 | 78000 | 0
| International |  |  | 630 | 38160 | 115000 | 153160 | 0 |  |  | 5 | 560 | 98000 | 0
|  |  |  | 800 | 78324 | 162000 | 240324 | 0 |  |  | 6 | 600 | 109000 | 0
|  |  | ACB | 1000 | 156000 | 280000 | 436000 | 0 |  | ACB | 7 | 800 | 200000 | 0
| Generation meter Required state are: |  |  | 1250/65kA | 242000 | 450000 | 692000 | 0 |  |  | 8 | 1000 | 200000 | 0
| Maharashtra |  |  | 1600 | 264000 | 500000 | 764000 | 0 |  |  | 9 | 1500 | 250000 | 0
| Rajasthan |  |  | 2000 | 312000 | 550000 | 862000 | 0 |  |  | 10 | 2000 | 300000 | 0
| Gujarat |  |  | 2500 | 342000 | 580000 | 922000 | 0 |  |  | 11 | >2000 | 380000 | 0
| Haryana |  |  | 3200 | 384000 | 610000 | 994000 | 0 | [5 empty] | 74000
| Delhi |  |  | 4000 | 396000 | 640000 | 1036000
| Bihar | [6 empty] | 381600
Punjab
Andhra Pradesh
| Telangana |  | No. of Sevice connection | 2
Madhya Pradesh
|  |  | Total no. of profile |  | 0
4PEL Scope
| Client Scope |  | Capacity (kWp) | BOM Cost (₹/Wp) |  |  |  |  | Capacity (kWp) | BOM Cost (₹/Wp)
| Using soil Trench |  | 400.52 | 14115230.596 |  |  |  |  | 5009 | 181375890
| Using New Cable Tray 300 mm |  | Calculation of Cost of BG | [5 empty] | Calculation of Cost of BG
| Trench Available, new cable tray 300 mm |  | 1 | Project Cost |  | 5.6534e+12 |  |  | 1 | Project Cost |  | 908511833010000
| Using Existing Cable Tray |  | 2 | PBG Amount | 0% | 0 |  |  | 2 | PBG Amount | 10% | 90851183301000
| Using New Cable Tray 600 mm |  | 3 | % of PBG Amount as Margin Money to be kept with Bank | 25% | 0 |  |  | 3 | % of PBG Amount as Margin Money to be kept with Bank | 25% | 22712795825250
| Trench Available, new cable tray 600 mm |  | 4 | FD interest gain on margin money | 7% | 0 |  |  | 4 | FD interest gain on margin money | 7% | 1.5899e+12
|  |  | 5 | Opportunity cost of margin money | 15% | 0 |  |  | 5 | Opportunity cost of margin money | 15% | 3.4069e+12
|  |  | 6 | Loss | #DIV/0! | 0 |  |  | 6 | Loss | 8% | 1.817e+12
| Gujarat |  | 7 | Annual cost of BG | 0.8% | 0 |  |  | 7 | Annual cost of BG | 0.8% | 726809466408
| Rajasthan |  | 8 | Total Cost To Company |  | 0 |  |  | 8 | Total Cost To Company |  | 2543833132428
| Tamil Nadu |  | 9 | No of Yrs BG is required to be maintained | 0 | 0 |  |  | 9 | No of Yrs BG is required to be maintained | 2 | 5087666264856
| Kerala |  | 10 | Per Wp Cost of BG with Plant capacity |  | 0 |  |  | 10 | Per Wp Cost of BG with Plant capacity |  | 1015704.984
Andhra Pradesh
|  |  | AC Capacity Ranges | Selection of Earthstrips
|  |  |  | Item | Strip Size
[5 empty] | Rooftop | Ground/Parking | Floating
|  |  | Upto 0-50kW AC | Module | 25X3 | 25X6 | 25X3
|  |  |  | MMS | 25X3 | 25X6 | 25X3
|  |  |  | Inverter | 25X3 | 25X6 | 25X3
|  |  |  | ACCB Panel | 25X3 | 25X6 | 25X3
|  |  |  | AC Cable tray | 25X3 | 25X6 | 25X3
|  |  |  | LA | 25X6 | 25X6 | 25X3
|  |  | Upto 51-150kW AC | Module | 25X3 | 25X6 | 25X3
|  |  |  | MMS | 25X3 | 25X6 | 25X3
|  |  |  | Inverter | 25X3 | 25X6 | 25X3
|  |  |  | ACCB Panel | 25X3 | 25X6 | 25X3
|  |  |  | Cable tray | 25X3 | 25X6 | 25X3
|  |  |  | LA | 25X6 | 25X6 | 25X3
|  |  | 151-500kW AC | Module | 25X3 | 25X6 | 25X3
|  |  |  | MMS | 25X3 | 25X6 | 25X6
|  |  |  | Inverter | 25X3 | 25X6 | 25X6
|  |  |  | ACCB Panel | 25X3 | 25X6 | 25X6
|  |  |  | Cable tray | 25X3 | 25X6 | 25X6
|  |  |  | LA | 25X3 | 25X6 | 25X6 |  | Back to top the of sheet
|  |  | 501kW to 1MW AC | Module | 25X3 | 25X6 | 25X3
|  |  |  | Structure | 25X3 | 25X6 | 25X6
|  |  |  | Inverter | 25x6 | 25X6/40x6 | 25X6/40x6
|  |  |  | ACCB Panel | 25x6 | 40X6 | 40X6
|  |  |  | Cable tray | 25x6 | 40X6 | 40X6
|  |  |  | LA | 25X6 | 25X6 | 25X6
|  |  | 1MW to 2MW AC | Module | 25X3 | 25X6 | 25X3
|  |  |  | MMS | 25X3 | 25X6 | 25X6
|  |  |  | Inverter | 25X6/40x6 | 25X6/40x6 | 25X6/40x6
|  |  |  | ACCB Panel | 40X6 | 50X6 | 40X6
|  |  |  | Cable tray | 40X6 | 50X6 | 40X6
|  |  |  | LA | 25X6 | 25X6 | 25X6
|  |  | 2MW to 5MW AC | Module | 25X3 | 25X6 | 25X3
|  |  |  | MMS | 25X3 | 25X6 | 25X6
|  |  |  | Inverter | 25X6/40x6 | 25X6/40x6 | 25X6/40x6
|  |  |  | ACCB Panel | 50X6 | 50X6 | 50X6
|  |  |  | Cable tray | 50X6 | 50X6 | 50X6
|  |  |  | LA | 25X6 | 25X6 | 25X6
368
[32 empty] | 10 |  |  | 100
[25 empty] | 8 | 30 | 14 | 50 | 0 | 0 | 120 | [19 empty] | 1
|  |  | S.No | String Inverter LT list
|  |  | 1 | Delta
|  |  | 2 | Sungrow
|  |  | 3 | Solis
|  |  | 4 | Hitachi
|  |  | 5 | SMA
|  |  | 6 | Solar Edge
|  |  | 7 | Huawei
|  |  | 8 | ABB
|  |  | 9 | Growatt
|  |  | 10 | Siening
|  |  | 11 | 0
|  |  | 12 | 0
|  |  | 13 | 0
Locked cell
Editable cell
|  | Sl.no. | Make | Rating
|  | 1 | Delta | Model | 100 |  | 70 | 66 | 50 | 30 |  | 20 | 15 | 10
|  |  |  | Price | 275000 |  | 240000 | 266000 | 197000 | 135000 |  | 121526 | 118000 | 80000
|  | 2 | Sungrow | Model | 100 |  |  |  | 50 | 33 |  | 20 | 15 | 10
|  |  |  | Price | 288500 |  |  |  | 152000 | 130000 |  | 98000 | 90000 | 75000
|  | 3 | Solis | Model | 150 | 125 | 80 | 60 | 50 | 30 | 25 | 20 | 15 | 10
|  |  |  | Price | 300000 | 290000 | 255000 | 135000 | 125000 | 95000 | 85000 | 70000 | 69000 | 75000
|  | 4 | Hitachi | Model |  |  | 70 | 60 | 50 | 33 | 30 | 25 | 20
|  |  |  | Price |  |  | 219450 | 207900 | 196350 | 138600 | 127050 | 121275 | 109725
|  | 5 | SMA | Model | 110 |  |  | 50 | 50 |  |  | 25 | 15
|  |  |  | Price | 415000 |  |  | 325050 | 194700 |  |  | 178750 | 171600
|  | 6 | Solar Edge | Model | 100 |  |  | 66 |  | 33 | 27 |  | 15
|  |  |  | Price | 275000 |  | 0 | 217000 | 0 | 147000 | 118000 |  | 100000
|  | 7 | Huawei | Model | 100 |  |  |  | 50 | 36
|  |  |  | Price | 280000 |  |  |  | 180000 | 160000
|  | 8 | ABB | Model | 100 |  |  |  | 50 |  | 27.6 |  | 20
|  |  |  | Price | 375100 |  |  |  | 215000 |  | 212000 |  | 190000
|  | 9 | Growatt | Model | 100 | 80 | 70 | 60 | 60 | 50 | 50 | 40 | 33 | 30
|  |  |  | Price | 212400 | 192552 | 184529 | 140402 | 168483 | 132380 | 160460 | 128368 | 111310 | 108310
|  | 10 | Siening | Model | 125 | 110 | 100 | 60 | 50 | 40 | 30 | 25 | 20 | 15
|  |  |  | Price | 255000 | 253000 | 240000 | 163000 | 163000 | 125000 | 90000 | 80000 | 70000 | 67000
|  | 11 | 0 | Model
Price
|  | 12 | 0 | Model
Price
|  | 13 | 0 | Model
Price
|  |  |  | Inverter Costings | 300000 | 290000 | 255000 | 135000 | 125000 | 95000 | 85000 | 70000 | 69000 | 75000
|  |  |  | Total Inv Costing | 600000
|  |  |  | per Watt Costing | 1.4981
Note on AG25: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: For Tamilnadu use Conventional LA
Note on AK25: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Railings are mandatory for tamilnadu and haryana for any module tilt
Note on AG26: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: For Tamilnadu use Conventional LA
Note on AK26: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Railings are mandatory for tamilnadu and haryana for any module tilt
Note on AG27: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: For Tamilnadu use Conventional LA
Note on AK27: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Railings are mandatory for tamilnadu and haryana for any module tilt
Note on AG28: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: For Tamilnadu use Conventional LA
Note on AK28: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Railings are mandatory for tamilnadu and haryana for any module tilt
Note on AG29: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: For Tamilnadu use Conventional LA
Note on AK29: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Railings are mandatory for tamilnadu and haryana for any module tilt
Note on AG30: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: For Tamilnadu use Conventional LA
Note on AK30: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Railings are mandatory for tamilnadu and haryana for any module tilt
Note on AG31: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: For Tamilnadu use Conventional LA
Note on AK31: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Railings are mandatory for tamilnadu and haryana for any module tilt
Note on AG32: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: For Tamilnadu use Conventional LA
Note on AK32: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Railings are mandatory for tamilnadu and haryana for any module tilt
Note on AG33: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: For Tamilnadu use Conventional LA
Note on AK33: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Railings are mandatory for tamilnadu and haryana for any module tilt
Note on AG34: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: For Tamilnadu use Conventional LA
Note on AK34: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Railings are mandatory for tamilnadu and haryana for any module tilt
Note on AG35: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: For Tamilnadu use Conventional LA
Note on AK35: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Railings are mandatory for tamilnadu and haryana for any module tilt
Note on AG36: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: For Tamilnadu use Conventional LA
Note on AK36: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Railings are mandatory for tamilnadu and haryana for any module tilt
Note on AG37: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: For Tamilnadu use Conventional LA
Note on AK37: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Railings are mandatory for tamilnadu and haryana for any module tilt
Note on AG38: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: For Tamilnadu use Conventional LA
Note on AK38: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Railings are mandatory for tamilnadu and haryana for any module tilt
Note on AG39: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: For Tamilnadu use Conventional LA
Note on AK39: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Railings are mandatory for tamilnadu and haryana for any module tilt
Note on AG40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: For Tamilnadu use Conventional LA
Note on AK40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Railings are mandatory for tamilnadu and haryana for any module tilt
Note on AG41: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: For Tamilnadu use Conventional LA
Note on AK41: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Railings are mandatory for tamilnadu and haryana for any module tilt
Note on AG42: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: For Tamilnadu use Conventional LA
Note on AK42: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Railings are mandatory for tamilnadu and haryana for any module tilt
Note on AG43: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: For Tamilnadu use Conventional LA
Note on AK43: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Railings are mandatory for tamilnadu and haryana for any module tilt
Note on AG44: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: For Tamilnadu use Conventional LA
Note on AK44: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Railings are mandatory for tamilnadu and haryana for any module tilt
Note on AG45: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: For Tamilnadu use Conventional LA
Note on AK45: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Railings are mandatory for tamilnadu and haryana for any module tilt
Note on AG46: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: For Tamilnadu use Conventional LA
Note on AK46: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Railings are mandatory for tamilnadu and haryana for any module tilt
Note on AG47: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: For Tamilnadu use Conventional LA
Note on AK47: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Railings are mandatory for tamilnadu and haryana for any module tilt
Note on AG48: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: For Tamilnadu use Conventional LA
Note on AK48: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Railings are mandatory for tamilnadu and haryana for any module tilt
Note on AG49: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: For Tamilnadu use Conventional LA
Note on AK49: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Railings are mandatory for tamilnadu and haryana for any module tilt
Note on AG50: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: For Tamilnadu use Conventional LA
Note on AK50: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Railings are mandatory for tamilnadu and haryana for any module tilt
Note on AG51: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: For Tamilnadu use Conventional LA
Note on AK51: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Railings are mandatory for tamilnadu and haryana for any module tilt
Note on AG52: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: For Tamilnadu use Conventional LA
Note on AK52: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Railings are mandatory for tamilnadu and haryana for any module tilt
Note on AG53: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: For Tamilnadu use Conventional LA
Note on AK53: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Railings are mandatory for tamilnadu and haryana for any module tilt
Note on AG54: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: For Tamilnadu use Conventional LA
Note on AK54: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Railings are mandatory for tamilnadu and haryana for any module tilt
Note on F386: Author: PBG Amount (X% of EPC Value)
Note on L386: Author: PBG Amount (X% of EPC Value)
Note on F393: Author: insert the 'No. of years" we are keeping PBG with customer
Note on L393: Author: insert the 'No. of years" we are keeping PBG with customer

## Cable Calcualtion (hidden)
Al. CABLE CAPACITY(3.5Core) in Sq.mm |  | 16 | 25 | 35 | 50 | 70 | 95 | 120 | 150 | 185 | 240 | 300 | 400
|  | 3x 16+16 | 3x25+16 | 3x35+16 | 3x50+25 | 3x70+35 | 3x95+50 | 3x120+70 | 3x150+70 | 3x185+95 | 3x240+120 | 3x300+150 | 3x400+185
Cable Amps in Al. Cond. Run in Ground |  | 74 | 94 | 113 | 133 | 164 | 196 | 223 | 249 | 282 | 326 | 367 | 418
Cable Amps in Al. Cond. Run in Air |  | 74 | 96 | 117 | 142 | 179 | 221 | 257 | 292 | 337 | 399 | 455 | 530
Total Derating factorb (K1*K2*K3*K4*K5*K6*K7) | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
Derated Current in Ground |  | 51.8 | 65.8 | 79.1 | 93.1 | 114.8 | 137.2 | 156.1 | 174.3 | 197.4 | 228.2 | 256.9 | 292.6
Derated Current in Air |  | 51.8 | 67.2 | 81.9 | 99.4 | 125.3 | 154.7 | 179.9 | 204.4 | 235.9 | 279.3 | 318.5 | 371
Resistance @ 90 degrees in ohm/Km |  | 2.44 | 1.54 | 1.11 | 0.82 | 0.567 | 0.41 | 0.324 | 0.264 | 0.21 | 0.16 | 0.128 | 0.1
Reactance @ 50HZ in ohm/Km |  | 0.0808 | 0.0805 | 0.0783 | 0.075 | 0.074 | 0.0724 | 0.0712 | 0.0716 | 0.0718 | 0.071 | 0.0705 | 0.0704
No.of amps need to carry on each phase (Amp) | 196.8297 | 196.8297 | 196.8297 | 196.8297 | 196.8297 | 196.8297 | 196.8297 | 196.8297 | 196.8297 | 196.8297 | 196.8297 | 196.8297 | 196.8297
No.of meters for run (Mtrs) | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170
No.of runs | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Operating Voltage | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415
Voltage drop of cable |  | 141.4091 | 89.25 | 64.3295 | 47.5227 | 32.8602 | 23.7614 | 18.7773 | 15.3 | 12.1705 | 9.2727 | 7.4182 | 5.7955
Voltage drop of cable% |  | 34.07% | 21.51% | 15.5% | 11.45% | 7.918% | 5.726% | 4.525% | 3.687% | 2.933% | 2.234% | 1.788% | 1.396%
If feasable in Ground | 2% | FAIL | FAIL | FAIL | FAIL | FAIL | FAIL | FAIL | FAIL | FAIL | FAIL | PASS | PASS
If feasable in Air |  | FAIL | FAIL | FAIL | FAIL | FAIL | FAIL | FAIL | FAIL | FAIL | FAIL | PASS | PASS
196.8297 | Amps
1
If feasable in Ground | 300 | Sqmm.
If feasable in Air | 300 | Sqmm.
Al. CABLE CAPACITY(3.5Core) in Sq.mm |  | 16 | 25 | 35 | 50 | 70 | 95 | 120 | 150 | 185 | 240 | 300 | 400
|  | 3x 16+16 | 3x25+16 | 3x35+16 | 3x50+25 | 3x70+35 | 3x95+50 | 3x120+70 | 3x150+70 | 3x185+95 | 3x240+120 | 3x300+150 | 3x400+185
Cable Amps in Al. Cond. Run in Ground |  | 74 | 94 | 113 | 133 | 164 | 196 | 223 | 249 | 282 | 326 | 367 | 418
Cable Amps in Al. Cond. Run in Air |  | 74 | 96 | 117 | 142 | 179 | 221 | 257 | 292 | 337 | 399 | 455 | 530
Total Derating factorb (K1*K2*K3*K4*K5*K6*K7) | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
Derated Current in Ground |  | 51.8 | 65.8 | 79.1 | 93.1 | 114.8 | 137.2 | 156.1 | 174.3 | 197.4 | 228.2 | 256.9 | 292.6
Derated Current in Air |  | 51.8 | 67.2 | 81.9 | 99.4 | 125.3 | 154.7 | 179.9 | 204.4 | 235.9 | 279.3 | 318.5 | 371
Resistance @ 90 degrees in ohm/Km |  | 2.44 | 1.54 | 1.11 | 0.82 | 0.567 | 0.41 | 0.324 | 0.264 | 0.21 | 0.16 | 0.128 | 0.1
Reactance @ 50HZ in ohm/Km |  | 0.0808 | 0.0805 | 0.0783 | 0.075 | 0.074 | 0.0724 | 0.0712 | 0.0716 | 0.0718 | 0.071 | 0.0705 | 0.0704
No.of amps need to carry on each phase (Amp) | 196.8297 | 196.8297 | 196.8297 | 196.8297 | 196.8297 | 196.8297 | 196.8297 | 196.8297 | 196.8297 | 196.8297 | 196.8297 | 196.8297 | 196.8297
No.of meters for run (Mtrs) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
No.of runs | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
Operating Voltage | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415
Voltage drop of cable |  | 91.5 | 57.75 | 41.625 | 30.75 | 21.2625 | 15.375 | 12.15 | 9.9 | 7.875 | 6 | 4.8 | 3.75
Voltage drop of cable% |  | 22.05% | 13.92% | 10.03% | 7.41% | 5.123% | 3.705% | 2.928% | 2.386% | 1.898% | 1.446% | 1.157% | 0.9036%
If feasable in Ground | 2% | FAIL | FAIL | FAIL | FAIL | FAIL | FAIL | FAIL | FAIL | PASS | PASS | PASS | PASS
If feasable in Air |  | FAIL | FAIL | FAIL | FAIL | FAIL | FAIL | FAIL | FAIL | PASS | PASS | PASS | PASS
196.8297 | Amps
2
If feasable in Ground | 185 | Sqmm.
If feasable in Air | 185 | Sqmm.
Al. CABLE CAPACITY(3.5Core) in Sq.mm |  | 16 | 25 | 35 | 50 | 70 | 95 | 120 | 150 | 185 | 240 | 300 | 400
|  | 3x 16+16 | 3x25+16 | 3x35+16 | 3x50+25 | 3x70+35 | 3x95+50 | 3x120+70 | 3x150+70 | 3x185+95 | 3x240+120 | 3x300+150 | 3x400+185
Cable Amps in Al. Cond. Run in Ground |  | 74 | 94 | 113 | 133 | 164 | 196 | 223 | 249 | 282 | 326 | 367 | 418
Cable Amps in Al. Cond. Run in Air |  | 74 | 96 | 117 | 142 | 179 | 221 | 257 | 292 | 337 | 399 | 455 | 530
Total Derating factorb (K1*K2*K3*K4*K5*K6*K7) | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
Derated Current in Ground |  | 51.8 | 65.8 | 79.1 | 93.1 | 114.8 | 137.2 | 156.1 | 174.3 | 197.4 | 228.2 | 256.9 | 292.6
Derated Current in Air |  | 51.8 | 67.2 | 81.9 | 99.4 | 125.3 | 154.7 | 179.9 | 204.4 | 235.9 | 279.3 | 318.5 | 371
Resistance @ 90 degrees in ohm/Km |  | 2.44 | 1.54 | 1.11 | 0.82 | 0.567 | 0.41 | 0.324 | 0.264 | 0.21 | 0.16 | 0.128 | 0.1
Reactance @ 50HZ in ohm/Km |  | 0.0808 | 0.0805 | 0.0783 | 0.075 | 0.074 | 0.0724 | 0.0712 | 0.0716 | 0.0718 | 0.071 | 0.0705 | 0.0704
No.of amps need to carry on each phase (Amp) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No.of meters for run (Mtrs) | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
No.of runs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Operating Voltage | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415
Voltage drop of cable |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Voltage drop of cable% |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
If feasable in Ground | 2% | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
If feasable in Air |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
0 | Amps
3
If feasable in Ground | #DIV/0! | Sqmm.
If feasable in Air | #DIV/0! | Sqmm.
Al. CABLE CAPACITY(3.5Core) in Sq.mm |  | 16 | 25 | 35 | 50 | 70 | 95 | 120 | 150 | 185 | 240 | 300 | 400
|  | 3x 16+16 | 3x25+16 | 3x35+16 | 3x50+25 | 3x70+35 | 3x95+50 | 3x120+70 | 3x150+70 | 3x185+95 | 3x240+120 | 3x300+150 | 3x400+185
Cable Amps in Al. Cond. Run in Ground |  | 74 | 94 | 113 | 133 | 164 | 196 | 223 | 249 | 282 | 326 | 367 | 418
Cable Amps in Al. Cond. Run in Air |  | 74 | 96 | 117 | 142 | 179 | 221 | 257 | 292 | 337 | 399 | 455 | 530
Total Derating factorb (K1*K2*K3*K4*K5*K6*K7) | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
Derated Current in Ground |  | 51.8 | 65.8 | 79.1 | 93.1 | 114.8 | 137.2 | 156.1 | 174.3 | 197.4 | 228.2 | 256.9 | 292.6
Derated Current in Air |  | 51.8 | 67.2 | 81.9 | 99.4 | 125.3 | 154.7 | 179.9 | 204.4 | 235.9 | 279.3 | 318.5 | 371
Resistance @ 90 degrees in ohm/Km |  | 2.44 | 1.54 | 1.11 | 0.82 | 0.567 | 0.41 | 0.324 | 0.264 | 0.21 | 0.16 | 0.128 | 0.1
Reactance @ 50HZ in ohm/Km |  | 0.0808 | 0.0805 | 0.0783 | 0.075 | 0.074 | 0.0724 | 0.0712 | 0.0716 | 0.0718 | 0.071 | 0.0705 | 0.0704
No.of amps need to carry on each phase (Amp) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No.of meters for run (Mtrs) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No.of runs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Operating Voltage | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415
Voltage drop of cable |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Voltage drop of cable% |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
If feasable in Ground | 2% | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
If feasable in Air |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
0 | Amps
4
If feasable in Ground | #DIV/0! | Sqmm.
If feasable in Air | #DIV/0! | Sqmm.
Al. CABLE CAPACITY(3.5Core) in Sq.mm |  | 16 | 25 | 35 | 50 | 70 | 95 | 120 | 150 | 185 | 240 | 300 | 400
|  | 3x 16+16 | 3x25+16 | 3x35+16 | 3x50+25 | 3x70+35 | 3x95+50 | 3x120+70 | 3x150+70 | 3x185+95 | 3x240+120 | 3x300+150 | 3x400+185
Cable Amps in Al. Cond. Run in Ground |  | 74 | 94 | 113 | 133 | 164 | 196 | 223 | 249 | 282 | 326 | 367 | 418
Cable Amps in Al. Cond. Run in Air |  | 74 | 96 | 117 | 142 | 179 | 221 | 257 | 292 | 337 | 399 | 455 | 530
Total Derating factorb (K1*K2*K3*K4*K5*K6*K7) | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
Derated Current in Ground |  | 51.8 | 65.8 | 79.1 | 93.1 | 114.8 | 137.2 | 156.1 | 174.3 | 197.4 | 228.2 | 256.9 | 292.6
Derated Current in Air |  | 51.8 | 67.2 | 81.9 | 99.4 | 125.3 | 154.7 | 179.9 | 204.4 | 235.9 | 279.3 | 318.5 | 371
Resistance @ 90 degrees in ohm/Km |  | 2.44 | 1.54 | 1.11 | 0.82 | 0.567 | 0.41 | 0.324 | 0.264 | 0.21 | 0.16 | 0.128 | 0.1
Reactance @ 50HZ in ohm/Km |  | 0.0808 | 0.0805 | 0.0783 | 0.075 | 0.074 | 0.0724 | 0.0712 | 0.0716 | 0.0718 | 0.071 | 0.0705 | 0.0704
No.of amps need to carry on each phase (Amp) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No.of meters for run (Mtrs) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No.of runs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Operating Voltage | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415
Voltage drop of cable |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Voltage drop of cable% |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
If feasable in Ground | 2% | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
If feasable in Air |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
0 | Amps
5
If feasable in Ground | #DIV/0! | Sqmm.
If feasable in Air | #DIV/0! | Sqmm.
Al. CABLE CAPACITY(3.5Core) in Sq.mm |  | 16 | 25 | 35 | 50 | 70 | 95 | 120 | 150 | 185 | 240 | 300 | 400
|  | 3x 16+16 | 3x25+16 | 3x35+16 | 3x50+25 | 3x70+35 | 3x95+50 | 3x120+70 | 3x150+70 | 3x185+95 | 3x240+120 | 3x300+150 | 3x400+185
Cable Amps in Al. Cond. Run in Ground |  | 74 | 94 | 113 | 133 | 164 | 196 | 223 | 249 | 282 | 326 | 367 | 418
Cable Amps in Al. Cond. Run in Air |  | 74 | 96 | 117 | 142 | 179 | 221 | 257 | 292 | 337 | 399 | 455 | 530
Total Derating factorb (K1*K2*K3*K4*K5*K6*K7) | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
Derated Current in Ground |  | 51.8 | 65.8 | 79.1 | 93.1 | 114.8 | 137.2 | 156.1 | 174.3 | 197.4 | 228.2 | 256.9 | 292.6
Derated Current in Air |  | 51.8 | 67.2 | 81.9 | 99.4 | 125.3 | 154.7 | 179.9 | 204.4 | 235.9 | 279.3 | 318.5 | 371
Resistance @ 90 degrees in ohm/Km |  | 2.44 | 1.54 | 1.11 | 0.82 | 0.567 | 0.41 | 0.324 | 0.264 | 0.21 | 0.16 | 0.128 | 0.1
Reactance @ 50HZ in ohm/Km |  | 0.0808 | 0.0805 | 0.0783 | 0.075 | 0.074 | 0.0724 | 0.0712 | 0.0716 | 0.0718 | 0.071 | 0.0705 | 0.0704
No.of amps need to carry on each phase (Amp) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No.of meters for run (Mtrs) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No.of runs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Operating Voltage | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415
Voltage drop of cable |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Voltage drop of cable% |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
If feasable in Ground | 2% | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
If feasable in Air |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
0 | Amps
6
If feasable in Ground | #DIV/0! | Sqmm.
If feasable in Air | #DIV/0! | Sqmm.
Al. CABLE CAPACITY(3.5Core) in Sq.mm |  | 16 | 25 | 35 | 50 | 70 | 95 | 120 | 150 | 185 | 240 | 300 | 400
|  | 3x 16+16 | 3x25+16 | 3x35+16 | 3x50+25 | 3x70+35 | 3x95+50 | 3x120+70 | 3x150+70 | 3x185+95 | 3x240+120 | 3x300+150 | 3x400+185
Cable Amps in Al. Cond. Run in Ground |  | 74 | 94 | 113 | 133 | 164 | 196 | 223 | 249 | 282 | 326 | 367 | 418
Cable Amps in Al. Cond. Run in Air |  | 74 | 96 | 117 | 142 | 179 | 221 | 257 | 292 | 337 | 399 | 455 | 530
Total Derating factorb (K1*K2*K3*K4*K5*K6*K7) | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
Derated Current in Ground |  | 51.8 | 65.8 | 79.1 | 93.1 | 114.8 | 137.2 | 156.1 | 174.3 | 197.4 | 228.2 | 256.9 | 292.6
Derated Current in Air |  | 51.8 | 67.2 | 81.9 | 99.4 | 125.3 | 154.7 | 179.9 | 204.4 | 235.9 | 279.3 | 318.5 | 371
Resistance @ 90 degrees in ohm/Km |  | 2.44 | 1.54 | 1.11 | 0.82 | 0.567 | 0.41 | 0.324 | 0.264 | 0.21 | 0.16 | 0.128 | 0.1
Reactance @ 50HZ in ohm/Km |  | 0.0808 | 0.0805 | 0.0783 | 0.075 | 0.074 | 0.0724 | 0.0712 | 0.0716 | 0.0718 | 0.071 | 0.0705 | 0.0704
No.of amps need to carry on each phase (Amp) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No.of meters for run (Mtrs) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No.of runs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Operating Voltage | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415
Voltage drop of cable |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Voltage drop of cable% |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
If feasable in Ground | 2% | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
If feasable in Air |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
0 | Amps
7
If feasable in Ground | #DIV/0! | Sqmm.
If feasable in Air | #DIV/0! | Sqmm.
Al. CABLE CAPACITY(3.5Core) in Sq.mm |  | 16 | 25 | 35 | 50 | 70 | 95 | 120 | 150 | 185 | 240 | 300 | 400
|  | 3x 16+16 | 3x25+16 | 3x35+16 | 3x50+25 | 3x70+35 | 3x95+50 | 3x120+70 | 3x150+70 | 3x185+95 | 3x240+120 | 3x300+150 | 3x400+185
Cable Amps in Al. Cond. Run in Ground |  | 74 | 94 | 113 | 133 | 164 | 196 | 223 | 249 | 282 | 326 | 367 | 418
Cable Amps in Al. Cond. Run in Air |  | 74 | 96 | 117 | 142 | 179 | 221 | 257 | 292 | 337 | 399 | 455 | 530
Total Derating factorb (K1*K2*K3*K4*K5*K6*K7) | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
Derated Current in Ground |  | 51.8 | 65.8 | 79.1 | 93.1 | 114.8 | 137.2 | 156.1 | 174.3 | 197.4 | 228.2 | 256.9 | 292.6
Derated Current in Air |  | 51.8 | 67.2 | 81.9 | 99.4 | 125.3 | 154.7 | 179.9 | 204.4 | 235.9 | 279.3 | 318.5 | 371
Resistance @ 90 degrees in ohm/Km |  | 2.44 | 1.54 | 1.11 | 0.82 | 0.567 | 0.41 | 0.324 | 0.264 | 0.21 | 0.16 | 0.128 | 0.1
Reactance @ 50HZ in ohm/Km |  | 0.0808 | 0.0805 | 0.0783 | 0.075 | 0.074 | 0.0724 | 0.0712 | 0.0716 | 0.0718 | 0.071 | 0.0705 | 0.0704
No.of amps need to carry on each phase (Amp) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No.of meters for run (Mtrs) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No.of runs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Operating Voltage | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415
Voltage drop of cable |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Voltage drop of cable% |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
If feasable in Ground | 2% | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
If feasable in Air |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
0 | Amps
8
If feasable in Ground | #DIV/0! | Sqmm.
If feasable in Air | #DIV/0! | Sqmm.
Al. CABLE CAPACITY(3.5Core) in Sq.mm |  | 16 | 25 | 35 | 50 | 70 | 95 | 120 | 150 | 185 | 240 | 300 | 400
|  | 3x 16+16 | 3x25+16 | 3x35+16 | 3x50+25 | 3x70+35 | 3x95+50 | 3x120+70 | 3x150+70 | 3x185+95 | 3x240+120 | 3x300+150 | 3x400+185
Cable Amps in Al. Cond. Run in Ground |  | 74 | 94 | 113 | 133 | 164 | 196 | 223 | 249 | 282 | 326 | 367 | 418
Cable Amps in Al. Cond. Run in Air |  | 74 | 96 | 117 | 142 | 179 | 221 | 257 | 292 | 337 | 399 | 455 | 530
Total Derating factorb (K1*K2*K3*K4*K5*K6*K7) | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
Derated Current in Ground |  | 51.8 | 65.8 | 79.1 | 93.1 | 114.8 | 137.2 | 156.1 | 174.3 | 197.4 | 228.2 | 256.9 | 292.6
Derated Current in Air |  | 51.8 | 67.2 | 81.9 | 99.4 | 125.3 | 154.7 | 179.9 | 204.4 | 235.9 | 279.3 | 318.5 | 371
Resistance @ 90 degrees in ohm/Km |  | 2.44 | 1.54 | 1.11 | 0.82 | 0.567 | 0.41 | 0.324 | 0.264 | 0.21 | 0.16 | 0.128 | 0.1
Reactance @ 50HZ in ohm/Km |  | 0.0808 | 0.0805 | 0.0783 | 0.075 | 0.074 | 0.0724 | 0.0712 | 0.0716 | 0.0718 | 0.071 | 0.0705 | 0.0704
No.of amps need to carry on each phase (Amp) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No.of meters for run (Mtrs) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No.of runs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Operating Voltage | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415
Voltage drop of cable |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Voltage drop of cable% |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
If feasable in Ground | 2% | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
If feasable in Air |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
0 | Amps
9
If feasable in Ground | #DIV/0! | Sqmm.
If feasable in Air | #DIV/0! | Sqmm.
Al. CABLE CAPACITY(3.5Core) in Sq.mm |  | 16 | 25 | 35 | 50 | 70 | 95 | 120 | 150 | 185 | 240 | 300 | 400
|  | 3x 16+16 | 3x25+16 | 3x35+16 | 3x50+25 | 3x70+35 | 3x95+50 | 3x120+70 | 3x150+70 | 3x185+95 | 3x240+120 | 3x300+150 | 3x400+185
Cable Amps in Al. Cond. Run in Ground |  | 74 | 94 | 113 | 133 | 164 | 196 | 223 | 249 | 282 | 326 | 367 | 418
Cable Amps in Al. Cond. Run in Air |  | 74 | 96 | 117 | 142 | 179 | 221 | 257 | 292 | 337 | 399 | 455 | 530
Total Derating factorb (K1*K2*K3*K4*K5*K6*K7) | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
Derated Current in Ground |  | 51.8 | 65.8 | 79.1 | 93.1 | 114.8 | 137.2 | 156.1 | 174.3 | 197.4 | 228.2 | 256.9 | 292.6
Derated Current in Air |  | 51.8 | 67.2 | 81.9 | 99.4 | 125.3 | 154.7 | 179.9 | 204.4 | 235.9 | 279.3 | 318.5 | 371
Resistance @ 90 degrees in ohm/Km |  | 2.44 | 1.54 | 1.11 | 0.82 | 0.567 | 0.41 | 0.324 | 0.264 | 0.21 | 0.16 | 0.128 | 0.1
Reactance @ 50HZ in ohm/Km |  | 0.0808 | 0.0805 | 0.0783 | 0.075 | 0.074 | 0.0724 | 0.0712 | 0.0716 | 0.0718 | 0.071 | 0.0705 | 0.0704
No.of amps need to carry on each phase (Amp) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No.of meters for run (Mtrs) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No.of runs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Operating Voltage | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415
Voltage drop of cable |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Voltage drop of cable% |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
If feasable in Ground | 2% | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
If feasable in Air |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
0 | Amps
10
If feasable in Ground | #DIV/0! | Sqmm.
If feasable in Air | #DIV/0! | Sqmm.
Al. CABLE CAPACITY(3.5Core) in Sq.mm |  | 16 | 25 | 35 | 50 | 70 | 95 | 120 | 150 | 185 | 240 | 300 | 400
|  | 3x 16+16 | 3x25+16 | 3x35+16 | 3x50+25 | 3x70+35 | 3x95+50 | 3x120+70 | 3x150+70 | 3x185+95 | 3x240+120 | 3x300+150 | 3x400+185
Cable Amps in Al. Cond. Run in Ground |  | 74 | 94 | 113 | 133 | 164 | 196 | 223 | 249 | 282 | 326 | 367 | 418
Cable Amps in Al. Cond. Run in Air |  | 74 | 96 | 117 | 142 | 179 | 221 | 257 | 292 | 337 | 399 | 455 | 530
Total Derating factorb (K1*K2*K3*K4*K5*K6*K7) | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
Derated Current in Ground |  | 51.8 | 65.8 | 79.1 | 93.1 | 114.8 | 137.2 | 156.1 | 174.3 | 197.4 | 228.2 | 256.9 | 292.6
Derated Current in Air |  | 51.8 | 67.2 | 81.9 | 99.4 | 125.3 | 154.7 | 179.9 | 204.4 | 235.9 | 279.3 | 318.5 | 371
Resistance @ 90 degrees in ohm/Km |  | 2.44 | 1.54 | 1.11 | 0.82 | 0.567 | 0.41 | 0.324 | 0.264 | 0.21 | 0.16 | 0.128 | 0.1
Reactance @ 50HZ in ohm/Km |  | 0.0808 | 0.0805 | 0.0783 | 0.075 | 0.074 | 0.0724 | 0.0712 | 0.0716 | 0.0718 | 0.071 | 0.0705 | 0.0704
No.of amps need to carry on each phase (Amp) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No.of meters for run (Mtrs) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No.of runs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Operating Voltage | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415
Voltage drop of cable |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Voltage drop of cable% |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
If feasable in Ground | 2% | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
If feasable in Air |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
0 | Amps
11
If feasable in Ground | #DIV/0! | Sqmm.
If feasable in Air | #DIV/0! | Sqmm.
Al. CABLE CAPACITY(3.5Core) in Sq.mm |  | 16 | 25 | 35 | 50 | 70 | 95 | 120 | 150 | 185 | 240 | 300 | 400
|  | 3x 16+16 | 3x25+16 | 3x35+16 | 3x50+25 | 3x70+35 | 3x95+50 | 3x120+70 | 3x150+70 | 3x185+95 | 3x240+120 | 3x300+150 | 3x400+185
Cable Amps in Al. Cond. Run in Ground |  | 74 | 94 | 113 | 133 | 164 | 196 | 223 | 249 | 282 | 326 | 367 | 418
Cable Amps in Al. Cond. Run in Air |  | 74 | 96 | 117 | 142 | 179 | 221 | 257 | 292 | 337 | 399 | 455 | 530
Total Derating factorb (K1*K2*K3*K4*K5*K6*K7) | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
Derated Current in Ground |  | 51.8 | 65.8 | 79.1 | 93.1 | 114.8 | 137.2 | 156.1 | 174.3 | 197.4 | 228.2 | 256.9 | 292.6
Derated Current in Air |  | 51.8 | 67.2 | 81.9 | 99.4 | 125.3 | 154.7 | 179.9 | 204.4 | 235.9 | 279.3 | 318.5 | 371
Resistance @ 90 degrees in ohm/Km |  | 2.44 | 1.54 | 1.11 | 0.82 | 0.567 | 0.41 | 0.324 | 0.264 | 0.21 | 0.16 | 0.128 | 0.1
Reactance @ 50HZ in ohm/Km |  | 0.0808 | 0.0805 | 0.0783 | 0.075 | 0.074 | 0.0724 | 0.0712 | 0.0716 | 0.0718 | 0.071 | 0.0705 | 0.0704
No.of amps need to carry on each phase (Amp) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No.of meters for run (Mtrs) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No.of runs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Operating Voltage | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415
Voltage drop of cable |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Voltage drop of cable% |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
If feasable in Ground | 2% | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
If feasable in Air |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
0 | Amps
12
If feasable in Ground | #DIV/0! | Sqmm.
If feasable in Air | #DIV/0! | Sqmm.
Al. CABLE CAPACITY(3.5Core) in Sq.mm |  | 16 | 25 | 35 | 50 | 70 | 95 | 120 | 150 | 185 | 240 | 300 | 400
|  | 3x 16+16 | 3x25+16 | 3x35+16 | 3x50+25 | 3x70+35 | 3x95+50 | 3x120+70 | 3x150+70 | 3x185+95 | 3x240+120 | 3x300+150 | 3x400+185
Cable Amps in Al. Cond. Run in Ground |  | 74 | 94 | 113 | 133 | 164 | 196 | 223 | 249 | 282 | 326 | 367 | 418
Cable Amps in Al. Cond. Run in Air |  | 74 | 96 | 117 | 142 | 179 | 221 | 257 | 292 | 337 | 399 | 455 | 530
Total Derating factorb (K1*K2*K3*K4*K5*K6*K7) | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
Derated Current in Ground |  | 51.8 | 65.8 | 79.1 | 93.1 | 114.8 | 137.2 | 156.1 | 174.3 | 197.4 | 228.2 | 256.9 | 292.6
Derated Current in Air |  | 51.8 | 67.2 | 81.9 | 99.4 | 125.3 | 154.7 | 179.9 | 204.4 | 235.9 | 279.3 | 318.5 | 371
Resistance @ 90 degrees in ohm/Km |  | 2.44 | 1.54 | 1.11 | 0.82 | 0.567 | 0.41 | 0.324 | 0.264 | 0.21 | 0.16 | 0.128 | 0.1
Reactance @ 50HZ in ohm/Km |  | 0.0808 | 0.0805 | 0.0783 | 0.075 | 0.074 | 0.0724 | 0.0712 | 0.0716 | 0.0718 | 0.071 | 0.0705 | 0.0704
No.of amps need to carry on each phase (Amp) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No.of meters for run (Mtrs) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No.of runs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Operating Voltage | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415
Voltage drop of cable |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Voltage drop of cable% |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
If feasable in Ground | 2% | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
If feasable in Air |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
0 | Amps
13
If feasable in Ground | #DIV/0! | Sqmm.
If feasable in Air | #DIV/0! | Sqmm.
Al. CABLE CAPACITY(3.5Core) in Sq.mm |  | 16 | 25 | 35 | 50 | 70 | 95 | 120 | 150 | 185 | 240 | 300 | 400
|  | 3x 16+16 | 3x25+16 | 3x35+16 | 3x50+25 | 3x70+35 | 3x95+50 | 3x120+70 | 3x150+70 | 3x185+95 | 3x240+120 | 3x300+150 | 3x400+185
Cable Amps in Al. Cond. Run in Ground |  | 74 | 94 | 113 | 133 | 164 | 196 | 223 | 249 | 282 | 326 | 367 | 418
Cable Amps in Al. Cond. Run in Air |  | 74 | 96 | 117 | 142 | 179 | 221 | 257 | 292 | 337 | 399 | 455 | 530
Total Derating factorb (K1*K2*K3*K4*K5*K6*K7) | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
Derated Current in Ground |  | 51.8 | 65.8 | 79.1 | 93.1 | 114.8 | 137.2 | 156.1 | 174.3 | 197.4 | 228.2 | 256.9 | 292.6
Derated Current in Air |  | 51.8 | 67.2 | 81.9 | 99.4 | 125.3 | 154.7 | 179.9 | 204.4 | 235.9 | 279.3 | 318.5 | 371
Resistance @ 90 degrees in ohm/Km |  | 2.44 | 1.54 | 1.11 | 0.82 | 0.567 | 0.41 | 0.324 | 0.264 | 0.21 | 0.16 | 0.128 | 0.1
Reactance @ 50HZ in ohm/Km |  | 0.0808 | 0.0805 | 0.0783 | 0.075 | 0.074 | 0.0724 | 0.0712 | 0.0716 | 0.0718 | 0.071 | 0.0705 | 0.0704
No.of amps need to carry on each phase (Amp) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No.of meters for run (Mtrs) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No.of runs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Operating Voltage | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415
Voltage drop of cable |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Voltage drop of cable% |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
If feasable in Ground | 2% | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
If feasable in Air |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
0 | Amps
14
If feasable in Ground | #DIV/0! | Sqmm.
If feasable in Air | #DIV/0! | Sqmm.
Al. CABLE CAPACITY(3.5Core) in Sq.mm |  | 16 | 25 | 35 | 50 | 70 | 95 | 120 | 150 | 185 | 240 | 300 | 400
|  | 3x 16+16 | 3x25+16 | 3x35+16 | 3x50+25 | 3x70+35 | 3x95+50 | 3x120+70 | 3x150+70 | 3x185+95 | 3x240+120 | 3x300+150 | 3x400+185
Cable Amps in Al. Cond. Run in Ground |  | 74 | 94 | 113 | 133 | 164 | 196 | 223 | 249 | 282 | 326 | 367 | 418
Cable Amps in Al. Cond. Run in Air |  | 74 | 96 | 117 | 142 | 179 | 221 | 257 | 292 | 337 | 399 | 455 | 530
Total Derating factorb (K1*K2*K3*K4*K5*K6*K7) | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
Derated Current in Ground |  | 51.8 | 65.8 | 79.1 | 93.1 | 114.8 | 137.2 | 156.1 | 174.3 | 197.4 | 228.2 | 256.9 | 292.6
Derated Current in Air |  | 51.8 | 67.2 | 81.9 | 99.4 | 125.3 | 154.7 | 179.9 | 204.4 | 235.9 | 279.3 | 318.5 | 371
Resistance @ 90 degrees in ohm/Km |  | 2.44 | 1.54 | 1.11 | 0.82 | 0.567 | 0.41 | 0.324 | 0.264 | 0.21 | 0.16 | 0.128 | 0.1
Reactance @ 50HZ in ohm/Km |  | 0.0808 | 0.0805 | 0.0783 | 0.075 | 0.074 | 0.0724 | 0.0712 | 0.0716 | 0.0718 | 0.071 | 0.0705 | 0.0704
No.of amps need to carry on each phase (Amp) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No.of meters for run (Mtrs) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No.of runs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Operating Voltage | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415
Voltage drop of cable |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Voltage drop of cable% |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
If feasable in Ground | 2% | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
If feasable in Air |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
0 | Amps
15
If feasable in Ground | #DIV/0! | Sqmm.
If feasable in Air | #DIV/0! | Sqmm.
Al. CABLE CAPACITY(3.5Core) in Sq.mm |  | 16 | 25 | 35 | 50 | 70 | 95 | 120 | 150 | 185 | 240 | 300 | 400
|  | 3x 16+16 | 3x25+16 | 3x35+16 | 3x50+25 | 3x70+35 | 3x95+50 | 3x120+70 | 3x150+70 | 3x185+95 | 3x240+120 | 3x300+150 | 3x400+185
Cable Amps in Al. Cond. Run in Ground |  | 74 | 94 | 113 | 133 | 164 | 196 | 223 | 249 | 282 | 326 | 367 | 418
Cable Amps in Al. Cond. Run in Air |  | 74 | 96 | 117 | 142 | 179 | 221 | 257 | 292 | 337 | 399 | 455 | 530
Total Derating factorb (K1*K2*K3*K4*K5*K6*K7) | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
Derated Current in Ground |  | 51.8 | 65.8 | 79.1 | 93.1 | 114.8 | 137.2 | 156.1 | 174.3 | 197.4 | 228.2 | 256.9 | 292.6
Derated Current in Air |  | 51.8 | 67.2 | 81.9 | 99.4 | 125.3 | 154.7 | 179.9 | 204.4 | 235.9 | 279.3 | 318.5 | 371
Resistance @ 90 degrees in ohm/Km |  | 2.44 | 1.54 | 1.11 | 0.82 | 0.567 | 0.41 | 0.324 | 0.264 | 0.21 | 0.16 | 0.128 | 0.1
Reactance @ 50HZ in ohm/Km |  | 0.0808 | 0.0805 | 0.0783 | 0.075 | 0.074 | 0.0724 | 0.0712 | 0.0716 | 0.0718 | 0.071 | 0.0705 | 0.0704
No.of amps need to carry on each phase (Amp) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No.of meters for run (Mtrs) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No.of runs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Operating Voltage | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415
Voltage drop of cable |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Voltage drop of cable% |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
If feasable in Ground | 2% | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
If feasable in Air |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
0 | Amps
16
If feasable in Ground | #DIV/0! | Sqmm.
If feasable in Air | #DIV/0! | Sqmm.
Al. CABLE CAPACITY(3.5Core) in Sq.mm |  | 16 | 25 | 35 | 50 | 70 | 95 | 120 | 150 | 185 | 240 | 300 | 400
|  | 3x 16+16 | 3x25+16 | 3x35+16 | 3x50+25 | 3x70+35 | 3x95+50 | 3x120+70 | 3x150+70 | 3x185+95 | 3x240+120 | 3x300+150 | 3x400+185
Cable Amps in Al. Cond. Run in Ground |  | 74 | 94 | 113 | 133 | 164 | 196 | 223 | 249 | 282 | 326 | 367 | 418
Cable Amps in Al. Cond. Run in Air |  | 74 | 96 | 117 | 142 | 179 | 221 | 257 | 292 | 337 | 399 | 455 | 530
Total Derating factorb (K1*K2*K3*K4*K5*K6*K7) | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
Derated Current in Ground |  | 51.8 | 65.8 | 79.1 | 93.1 | 114.8 | 137.2 | 156.1 | 174.3 | 197.4 | 228.2 | 256.9 | 292.6
Derated Current in Air |  | 51.8 | 67.2 | 81.9 | 99.4 | 125.3 | 154.7 | 179.9 | 204.4 | 235.9 | 279.3 | 318.5 | 371
Resistance @ 90 degrees in ohm/Km |  | 2.44 | 1.54 | 1.11 | 0.82 | 0.567 | 0.41 | 0.324 | 0.264 | 0.21 | 0.16 | 0.128 | 0.1
Reactance @ 50HZ in ohm/Km |  | 0.0808 | 0.0805 | 0.0783 | 0.075 | 0.074 | 0.0724 | 0.0712 | 0.0716 | 0.0718 | 0.071 | 0.0705 | 0.0704
No.of amps need to carry on each phase (Amp) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No.of meters for run (Mtrs) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No.of runs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Operating Voltage | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415
Voltage drop of cable |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Voltage drop of cable% |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
If feasable in Ground | 2% | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
If feasable in Air |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
0 | Amps
17
If feasable in Ground | #DIV/0! | Sqmm.
If feasable in Air | #DIV/0! | Sqmm.
Al. CABLE CAPACITY(3.5Core) in Sq.mm |  | 16 | 25 | 35 | 50 | 70 | 95 | 120 | 150 | 185 | 240 | 300 | 400
|  | 3x 16+16 | 3x25+16 | 3x35+16 | 3x50+25 | 3x70+35 | 3x95+50 | 3x120+70 | 3x150+70 | 3x185+95 | 3x240+120 | 3x300+150 | 3x400+185
Cable Amps in Al. Cond. Run in Ground |  | 74 | 94 | 113 | 133 | 164 | 196 | 223 | 249 | 282 | 326 | 367 | 418
Cable Amps in Al. Cond. Run in Air |  | 74 | 96 | 117 | 142 | 179 | 221 | 257 | 292 | 337 | 399 | 455 | 530
Total Derating factorb (K1*K2*K3*K4*K5*K6*K7) | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
Derated Current in Ground |  | 51.8 | 65.8 | 79.1 | 93.1 | 114.8 | 137.2 | 156.1 | 174.3 | 197.4 | 228.2 | 256.9 | 292.6
Derated Current in Air |  | 51.8 | 67.2 | 81.9 | 99.4 | 125.3 | 154.7 | 179.9 | 204.4 | 235.9 | 279.3 | 318.5 | 371
Resistance @ 90 degrees in ohm/Km |  | 2.44 | 1.54 | 1.11 | 0.82 | 0.567 | 0.41 | 0.324 | 0.264 | 0.21 | 0.16 | 0.128 | 0.1
Reactance @ 50HZ in ohm/Km |  | 0.0808 | 0.0805 | 0.0783 | 0.075 | 0.074 | 0.0724 | 0.0712 | 0.0716 | 0.0718 | 0.071 | 0.0705 | 0.0704
No.of amps need to carry on each phase (Amp) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No.of meters for run (Mtrs) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No.of runs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Operating Voltage | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415
Voltage drop of cable |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Voltage drop of cable% |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
If feasable in Ground | 2% | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
If feasable in Air |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
0 | Amps
18
If feasable in Ground | #DIV/0! | Sqmm.
If feasable in Air | #DIV/0! | Sqmm.
Al. CABLE CAPACITY(3.5Core) in Sq.mm |  | 16 | 25 | 35 | 50 | 70 | 95 | 120 | 150 | 185 | 240 | 300 | 400
|  | 3x 16+16 | 3x25+16 | 3x35+16 | 3x50+25 | 3x70+35 | 3x95+50 | 3x120+70 | 3x150+70 | 3x185+95 | 3x240+120 | 3x300+150 | 3x400+185
Cable Amps in Al. Cond. Run in Ground |  | 74 | 94 | 113 | 133 | 164 | 196 | 223 | 249 | 282 | 326 | 367 | 418
Cable Amps in Al. Cond. Run in Air |  | 74 | 96 | 117 | 142 | 179 | 221 | 257 | 292 | 337 | 399 | 455 | 530
Total Derating factorb (K1*K2*K3*K4*K5*K6*K7) | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
Derated Current in Ground |  | 51.8 | 65.8 | 79.1 | 93.1 | 114.8 | 137.2 | 156.1 | 174.3 | 197.4 | 228.2 | 256.9 | 292.6
Derated Current in Air |  | 51.8 | 67.2 | 81.9 | 99.4 | 125.3 | 154.7 | 179.9 | 204.4 | 235.9 | 279.3 | 318.5 | 371
Resistance @ 90 degrees in ohm/Km |  | 2.44 | 1.54 | 1.11 | 0.82 | 0.567 | 0.41 | 0.324 | 0.264 | 0.21 | 0.16 | 0.128 | 0.1
Reactance @ 50HZ in ohm/Km |  | 0.0808 | 0.0805 | 0.0783 | 0.075 | 0.074 | 0.0724 | 0.0712 | 0.0716 | 0.0718 | 0.071 | 0.0705 | 0.0704
No.of amps need to carry on each phase (Amp) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No.of meters for run (Mtrs) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No.of runs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Operating Voltage | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415
Voltage drop of cable |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Voltage drop of cable% |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
If feasable in Ground | 2% | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
If feasable in Air |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
0 | Amps
19
If feasable in Ground | #DIV/0! | Sqmm.
If feasable in Air | #DIV/0! | Sqmm.
Al. CABLE CAPACITY(3.5Core) in Sq.mm |  | 16 | 25 | 35 | 50 | 70 | 95 | 120 | 150 | 185 | 240 | 300 | 400
|  | 3x 16+16 | 3x25+16 | 3x35+16 | 3x50+25 | 3x70+35 | 3x95+50 | 3x120+70 | 3x150+70 | 3x185+95 | 3x240+120 | 3x300+150 | 3x400+185
Cable Amps in Al. Cond. Run in Ground |  | 74 | 94 | 113 | 133 | 164 | 196 | 223 | 249 | 282 | 326 | 367 | 418
Cable Amps in Al. Cond. Run in Air |  | 74 | 96 | 117 | 142 | 179 | 221 | 257 | 292 | 337 | 399 | 455 | 530
Total Derating factorb (K1*K2*K3*K4*K5*K6*K7) | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
Derated Current in Ground |  | 51.8 | 65.8 | 79.1 | 93.1 | 114.8 | 137.2 | 156.1 | 174.3 | 197.4 | 228.2 | 256.9 | 292.6
Derated Current in Air |  | 51.8 | 67.2 | 81.9 | 99.4 | 125.3 | 154.7 | 179.9 | 204.4 | 235.9 | 279.3 | 318.5 | 371
Resistance @ 90 degrees in ohm/Km |  | 2.44 | 1.54 | 1.11 | 0.82 | 0.567 | 0.41 | 0.324 | 0.264 | 0.21 | 0.16 | 0.128 | 0.1
Reactance @ 50HZ in ohm/Km |  | 0.0808 | 0.0805 | 0.0783 | 0.075 | 0.074 | 0.0724 | 0.0712 | 0.0716 | 0.0718 | 0.071 | 0.0705 | 0.0704
No.of amps need to carry on each phase (Amp) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No.of meters for run (Mtrs) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No.of runs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Operating Voltage | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415
Voltage drop of cable |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Voltage drop of cable% |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
If feasable in Ground | 2% | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
If feasable in Air |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
0 | Amps
20
If feasable in Ground | #DIV/0! | Sqmm.
If feasable in Air | #DIV/0! | Sqmm.
Al. CABLE CAPACITY(3.5Core) in Sq.mm |  | 16 | 25 | 35 | 50 | 70 | 95 | 120 | 150 | 185 | 240 | 300 | 400
|  | 3x 16+16 | 3x25+16 | 3x35+16 | 3x50+25 | 3x70+35 | 3x95+50 | 3x120+70 | 3x150+70 | 3x185+95 | 3x240+120 | 3x300+150 | 3x400+185
Cable Amps in Al. Cond. Run in Ground |  | 74 | 94 | 113 | 133 | 164 | 196 | 223 | 249 | 282 | 326 | 367 | 418
Cable Amps in Al. Cond. Run in Air |  | 74 | 96 | 117 | 142 | 179 | 221 | 257 | 292 | 337 | 399 | 455 | 530
Total Derating factorb (K1*K2*K3*K4*K5*K6*K7) | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
Derated Current in Ground |  | 51.8 | 65.8 | 79.1 | 93.1 | 114.8 | 137.2 | 156.1 | 174.3 | 197.4 | 228.2 | 256.9 | 292.6
Derated Current in Air |  | 51.8 | 67.2 | 81.9 | 99.4 | 125.3 | 154.7 | 179.9 | 204.4 | 235.9 | 279.3 | 318.5 | 371
Resistance @ 90 degrees in ohm/Km |  | 2.44 | 1.54 | 1.11 | 0.82 | 0.567 | 0.41 | 0.324 | 0.264 | 0.21 | 0.16 | 0.128 | 0.1
Reactance @ 50HZ in ohm/Km |  | 0.0808 | 0.0805 | 0.0783 | 0.075 | 0.074 | 0.0724 | 0.0712 | 0.0716 | 0.0718 | 0.071 | 0.0705 | 0.0704
No.of amps need to carry on each phase (Amp) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No.of meters for run (Mtrs) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No.of runs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Operating Voltage | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415
Voltage drop of cable |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Voltage drop of cable% |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
If feasable in Ground | 2% | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
If feasable in Air |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
0 | Amps
21
If feasable in Ground | #DIV/0! | Sqmm.
If feasable in Air | #DIV/0! | Sqmm.
Al. CABLE CAPACITY(3.5Core) in Sq.mm |  | 16 | 25 | 35 | 50 | 70 | 95 | 120 | 150 | 185 | 240 | 300 | 400
|  | 3x 16+16 | 3x25+16 | 3x35+16 | 3x50+25 | 3x70+35 | 3x95+50 | 3x120+70 | 3x150+70 | 3x185+95 | 3x240+120 | 3x300+150 | 3x400+185
Cable Amps in Al. Cond. Run in Ground |  | 74 | 94 | 113 | 133 | 164 | 196 | 223 | 249 | 282 | 326 | 367 | 418
Cable Amps in Al. Cond. Run in Air |  | 74 | 96 | 117 | 142 | 179 | 221 | 257 | 292 | 337 | 399 | 455 | 530
Total Derating factorb (K1*K2*K3*K4*K5*K6*K7) | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
Derated Current in Ground |  | 51.8 | 65.8 | 79.1 | 93.1 | 114.8 | 137.2 | 156.1 | 174.3 | 197.4 | 228.2 | 256.9 | 292.6
Derated Current in Air |  | 51.8 | 67.2 | 81.9 | 99.4 | 125.3 | 154.7 | 179.9 | 204.4 | 235.9 | 279.3 | 318.5 | 371
Resistance @ 90 degrees in ohm/Km |  | 2.44 | 1.54 | 1.11 | 0.82 | 0.567 | 0.41 | 0.324 | 0.264 | 0.21 | 0.16 | 0.128 | 0.1
Reactance @ 50HZ in ohm/Km |  | 0.0808 | 0.0805 | 0.0783 | 0.075 | 0.074 | 0.0724 | 0.0712 | 0.0716 | 0.0718 | 0.071 | 0.0705 | 0.0704
No.of amps need to carry on each phase (Amp) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No.of meters for run (Mtrs) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No.of runs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Operating Voltage | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415
Voltage drop of cable |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Voltage drop of cable% |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
If feasable in Ground | 2% | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
If feasable in Air |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
0 | Amps
22
If feasable in Ground | #DIV/0! | Sqmm.
If feasable in Air | #DIV/0! | Sqmm.
Al. CABLE CAPACITY(3.5Core) in Sq.mm |  | 16 | 25 | 35 | 50 | 70 | 95 | 120 | 150 | 185 | 240 | 300 | 400
|  | 3x 16+16 | 3x25+16 | 3x35+16 | 3x50+25 | 3x70+35 | 3x95+50 | 3x120+70 | 3x150+70 | 3x185+95 | 3x240+120 | 3x300+150 | 3x400+185
Cable Amps in Al. Cond. Run in Ground |  | 74 | 94 | 113 | 133 | 164 | 196 | 223 | 249 | 282 | 326 | 367 | 418
Cable Amps in Al. Cond. Run in Air |  | 74 | 96 | 117 | 142 | 179 | 221 | 257 | 292 | 337 | 399 | 455 | 530
Total Derating factorb (K1*K2*K3*K4*K5*K6*K7) | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
Derated Current in Ground |  | 51.8 | 65.8 | 79.1 | 93.1 | 114.8 | 137.2 | 156.1 | 174.3 | 197.4 | 228.2 | 256.9 | 292.6
Derated Current in Air |  | 51.8 | 67.2 | 81.9 | 99.4 | 125.3 | 154.7 | 179.9 | 204.4 | 235.9 | 279.3 | 318.5 | 371
Resistance @ 90 degrees in ohm/Km |  | 2.44 | 1.54 | 1.11 | 0.82 | 0.567 | 0.41 | 0.324 | 0.264 | 0.21 | 0.16 | 0.128 | 0.1
Reactance @ 50HZ in ohm/Km |  | 0.0808 | 0.0805 | 0.0783 | 0.075 | 0.074 | 0.0724 | 0.0712 | 0.0716 | 0.0718 | 0.071 | 0.0705 | 0.0704
No.of amps need to carry on each phase (Amp) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No.of meters for run (Mtrs) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No.of runs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Operating Voltage | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415
Voltage drop of cable |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Voltage drop of cable% |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
If feasable in Ground | 2% | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
If feasable in Air |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
0 | Amps
23
If feasable in Ground | #DIV/0! | Sqmm.
If feasable in Air | #DIV/0! | Sqmm.
Al. CABLE CAPACITY(3.5Core) in Sq.mm |  | 16 | 25 | 35 | 50 | 70 | 95 | 120 | 150 | 185 | 240 | 300 | 400
|  | 3x 16+16 | 3x25+16 | 3x35+16 | 3x50+25 | 3x70+35 | 3x95+50 | 3x120+70 | 3x150+70 | 3x185+95 | 3x240+120 | 3x300+150 | 3x400+185
Cable Amps in Al. Cond. Run in Ground |  | 74 | 94 | 113 | 133 | 164 | 196 | 223 | 249 | 282 | 326 | 367 | 418
Cable Amps in Al. Cond. Run in Air |  | 74 | 96 | 117 | 142 | 179 | 221 | 257 | 292 | 337 | 399 | 455 | 530
Total Derating factorb (K1*K2*K3*K4*K5*K6*K7) | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
Derated Current in Ground |  | 51.8 | 65.8 | 79.1 | 93.1 | 114.8 | 137.2 | 156.1 | 174.3 | 197.4 | 228.2 | 256.9 | 292.6
Derated Current in Air |  | 51.8 | 67.2 | 81.9 | 99.4 | 125.3 | 154.7 | 179.9 | 204.4 | 235.9 | 279.3 | 318.5 | 371
Resistance @ 90 degrees in ohm/Km |  | 2.44 | 1.54 | 1.11 | 0.82 | 0.567 | 0.41 | 0.324 | 0.264 | 0.21 | 0.16 | 0.128 | 0.1
Reactance @ 50HZ in ohm/Km |  | 0.0808 | 0.0805 | 0.0783 | 0.075 | 0.074 | 0.0724 | 0.0712 | 0.0716 | 0.0718 | 0.071 | 0.0705 | 0.0704
No.of amps need to carry on each phase (Amp) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No.of meters for run (Mtrs) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No.of runs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Operating Voltage | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415
Voltage drop of cable |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Voltage drop of cable% |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
If feasable in Ground | 2% | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
If feasable in Air |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
0 | Amps
24
If feasable in Ground | #DIV/0! | Sqmm.
If feasable in Air | #DIV/0! | Sqmm.
Al. CABLE CAPACITY(3.5Core) in Sq.mm |  | 16 | 25 | 35 | 50 | 70 | 95 | 120 | 150 | 185 | 240 | 300 | 400
|  | 3x 16+16 | 3x25+16 | 3x35+16 | 3x50+25 | 3x70+35 | 3x95+50 | 3x120+70 | 3x150+70 | 3x185+95 | 3x240+120 | 3x300+150 | 3x400+185
Cable Amps in Al. Cond. Run in Ground |  | 74 | 94 | 113 | 133 | 164 | 196 | 223 | 249 | 282 | 326 | 367 | 418
Cable Amps in Al. Cond. Run in Air |  | 74 | 96 | 117 | 142 | 179 | 221 | 257 | 292 | 337 | 399 | 455 | 530
Total Derating factorb (K1*K2*K3*K4*K5*K6*K7) | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
Derated Current in Ground |  | 51.8 | 65.8 | 79.1 | 93.1 | 114.8 | 137.2 | 156.1 | 174.3 | 197.4 | 228.2 | 256.9 | 292.6
Derated Current in Air |  | 51.8 | 67.2 | 81.9 | 99.4 | 125.3 | 154.7 | 179.9 | 204.4 | 235.9 | 279.3 | 318.5 | 371
Resistance @ 90 degrees in ohm/Km |  | 2.44 | 1.54 | 1.11 | 0.82 | 0.567 | 0.41 | 0.324 | 0.264 | 0.21 | 0.16 | 0.128 | 0.1
Reactance @ 50HZ in ohm/Km |  | 0.0808 | 0.0805 | 0.0783 | 0.075 | 0.074 | 0.0724 | 0.0712 | 0.0716 | 0.0718 | 0.071 | 0.0705 | 0.0704
No.of amps need to carry on each phase (Amp) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No.of meters for run (Mtrs) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No.of runs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Operating Voltage | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415
Voltage drop of cable |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Voltage drop of cable% |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
If feasable in Ground | 2% | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
If feasable in Air |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
0 | Amps
25
If feasable in Ground | #DIV/0! | Sqmm.
If feasable in Air | #DIV/0! | Sqmm.
Al. CABLE CAPACITY(3.5Core) in Sq.mm |  | 16 | 25 | 35 | 50 | 70 | 95 | 120 | 150 | 185 | 240 | 300 | 400
|  | 3x 16+16 | 3x25+16 | 3x35+16 | 3x50+25 | 3x70+35 | 3x95+50 | 3x120+70 | 3x150+70 | 3x185+95 | 3x240+120 | 3x300+150 | 3x400+185
Cable Amps in Al. Cond. Run in Ground |  | 74 | 94 | 113 | 133 | 164 | 196 | 223 | 249 | 282 | 326 | 367 | 418
Cable Amps in Al. Cond. Run in Air |  | 74 | 96 | 117 | 142 | 179 | 221 | 257 | 292 | 337 | 399 | 455 | 530
Total Derating factorb (K1*K2*K3*K4*K5*K6*K7) | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
Derated Current in Ground |  | 51.8 | 65.8 | 79.1 | 93.1 | 114.8 | 137.2 | 156.1 | 174.3 | 197.4 | 228.2 | 256.9 | 292.6
Derated Current in Air |  | 51.8 | 67.2 | 81.9 | 99.4 | 125.3 | 154.7 | 179.9 | 204.4 | 235.9 | 279.3 | 318.5 | 371
Resistance @ 90 degrees in ohm/Km |  | 2.44 | 1.54 | 1.11 | 0.82 | 0.567 | 0.41 | 0.324 | 0.264 | 0.21 | 0.16 | 0.128 | 0.1
Reactance @ 50HZ in ohm/Km |  | 0.0808 | 0.0805 | 0.0783 | 0.075 | 0.074 | 0.0724 | 0.0712 | 0.0716 | 0.0718 | 0.071 | 0.0705 | 0.0704
No.of amps need to carry on each phase (Amp) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No.of meters for run (Mtrs) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No.of runs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Operating Voltage | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415
Voltage drop of cable |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Voltage drop of cable% |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
If feasable in Ground | 2% | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
If feasable in Air |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
0 | Amps
26
If feasable in Ground | #DIV/0! | Sqmm.
If feasable in Air | #DIV/0! | Sqmm.
Al. CABLE CAPACITY(3.5Core) in Sq.mm |  | 16 | 25 | 35 | 50 | 70 | 95 | 120 | 150 | 185 | 240 | 300 | 400
|  | 3x 16+16 | 3x25+16 | 3x35+16 | 3x50+25 | 3x70+35 | 3x95+50 | 3x120+70 | 3x150+70 | 3x185+95 | 3x240+120 | 3x300+150 | 3x400+185
Cable Amps in Al. Cond. Run in Ground |  | 74 | 94 | 113 | 133 | 164 | 196 | 223 | 249 | 282 | 326 | 367 | 418
Cable Amps in Al. Cond. Run in Air |  | 74 | 96 | 117 | 142 | 179 | 221 | 257 | 292 | 337 | 399 | 455 | 530
Total Derating factorb (K1*K2*K3*K4*K5*K6*K7) | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
Derated Current in Ground |  | 51.8 | 65.8 | 79.1 | 93.1 | 114.8 | 137.2 | 156.1 | 174.3 | 197.4 | 228.2 | 256.9 | 292.6
Derated Current in Air |  | 51.8 | 67.2 | 81.9 | 99.4 | 125.3 | 154.7 | 179.9 | 204.4 | 235.9 | 279.3 | 318.5 | 371
Resistance @ 90 degrees in ohm/Km |  | 2.44 | 1.54 | 1.11 | 0.82 | 0.567 | 0.41 | 0.324 | 0.264 | 0.21 | 0.16 | 0.128 | 0.1
Reactance @ 50HZ in ohm/Km |  | 0.0808 | 0.0805 | 0.0783 | 0.075 | 0.074 | 0.0724 | 0.0712 | 0.0716 | 0.0718 | 0.071 | 0.0705 | 0.0704
No.of amps need to carry on each phase (Amp) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No.of meters for run (Mtrs) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No.of runs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Operating Voltage | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415
Voltage drop of cable |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Voltage drop of cable% |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
If feasable in Ground | 2% | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
If feasable in Air |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
0 | Amps
27
If feasable in Ground | #DIV/0! | Sqmm.
If feasable in Air | #DIV/0! | Sqmm.
Al. CABLE CAPACITY(3.5Core) in Sq.mm |  | 16 | 25 | 35 | 50 | 70 | 95 | 120 | 150 | 185 | 240 | 300 | 400
|  | 3x 16+16 | 3x25+16 | 3x35+16 | 3x50+25 | 3x70+35 | 3x95+50 | 3x120+70 | 3x150+70 | 3x185+95 | 3x240+120 | 3x300+150 | 3x400+185
Cable Amps in Al. Cond. Run in Ground |  | 74 | 94 | 113 | 133 | 164 | 196 | 223 | 249 | 282 | 326 | 367 | 418
Cable Amps in Al. Cond. Run in Air |  | 74 | 96 | 117 | 142 | 179 | 221 | 257 | 292 | 337 | 399 | 455 | 530
Total Derating factorb (K1*K2*K3*K4*K5*K6*K7) | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
Derated Current in Ground |  | 51.8 | 65.8 | 79.1 | 93.1 | 114.8 | 137.2 | 156.1 | 174.3 | 197.4 | 228.2 | 256.9 | 292.6
Derated Current in Air |  | 51.8 | 67.2 | 81.9 | 99.4 | 125.3 | 154.7 | 179.9 | 204.4 | 235.9 | 279.3 | 318.5 | 371
Resistance @ 90 degrees in ohm/Km |  | 2.44 | 1.54 | 1.11 | 0.82 | 0.567 | 0.41 | 0.324 | 0.264 | 0.21 | 0.16 | 0.128 | 0.1
Reactance @ 50HZ in ohm/Km |  | 0.0808 | 0.0805 | 0.0783 | 0.075 | 0.074 | 0.0724 | 0.0712 | 0.0716 | 0.0718 | 0.071 | 0.0705 | 0.0704
No.of amps need to carry on each phase (Amp) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No.of meters for run (Mtrs) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No.of runs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Operating Voltage | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415
Voltage drop of cable |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Voltage drop of cable% |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
If feasable in Ground | 2% | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
If feasable in Air |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
0 | Amps
28
If feasable in Ground | #DIV/0! | Sqmm.
If feasable in Air | #DIV/0! | Sqmm.
Al. CABLE CAPACITY(3.5Core) in Sq.mm |  | 16 | 25 | 35 | 50 | 70 | 95 | 120 | 150 | 185 | 240 | 300 | 400
|  | 3x 16+16 | 3x25+16 | 3x35+16 | 3x50+25 | 3x70+35 | 3x95+50 | 3x120+70 | 3x150+70 | 3x185+95 | 3x240+120 | 3x300+150 | 3x400+185
Cable Amps in Al. Cond. Run in Ground |  | 74 | 94 | 113 | 133 | 164 | 196 | 223 | 249 | 282 | 326 | 367 | 418
Cable Amps in Al. Cond. Run in Air |  | 74 | 96 | 117 | 142 | 179 | 221 | 257 | 292 | 337 | 399 | 455 | 530
Total Derating factorb (K1*K2*K3*K4*K5*K6*K7) | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
Derated Current in Ground |  | 51.8 | 65.8 | 79.1 | 93.1 | 114.8 | 137.2 | 156.1 | 174.3 | 197.4 | 228.2 | 256.9 | 292.6
Derated Current in Air |  | 51.8 | 67.2 | 81.9 | 99.4 | 125.3 | 154.7 | 179.9 | 204.4 | 235.9 | 279.3 | 318.5 | 371
Resistance @ 90 degrees in ohm/Km |  | 2.44 | 1.54 | 1.11 | 0.82 | 0.567 | 0.41 | 0.324 | 0.264 | 0.21 | 0.16 | 0.128 | 0.1
Reactance @ 50HZ in ohm/Km |  | 0.0808 | 0.0805 | 0.0783 | 0.075 | 0.074 | 0.0724 | 0.0712 | 0.0716 | 0.0718 | 0.071 | 0.0705 | 0.0704
No.of amps need to carry on each phase (Amp) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No.of meters for run (Mtrs) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No.of runs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Operating Voltage | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415
Voltage drop of cable |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Voltage drop of cable% |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
If feasable in Ground | 2% | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
If feasable in Air |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
0 | Amps
29
If feasable in Ground | #DIV/0! | Sqmm.
If feasable in Air | #DIV/0! | Sqmm.
Al. CABLE CAPACITY(3.5Core) in Sq.mm |  | 16 | 25 | 35 | 50 | 70 | 95 | 120 | 150 | 185 | 240 | 300 | 400
|  | 3x 16+16 | 3x25+16 | 3x35+16 | 3x50+25 | 3x70+35 | 3x95+50 | 3x120+70 | 3x150+70 | 3x185+95 | 3x240+120 | 3x300+150 | 3x400+185
Cable Amps in Al. Cond. Run in Ground |  | 74 | 94 | 113 | 133 | 164 | 196 | 223 | 249 | 282 | 326 | 367 | 418
Cable Amps in Al. Cond. Run in Air |  | 74 | 96 | 117 | 142 | 179 | 221 | 257 | 292 | 337 | 399 | 455 | 530
Total Derating factorb (K1*K2*K3*K4*K5*K6*K7) | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
Derated Current in Ground |  | 51.8 | 65.8 | 79.1 | 93.1 | 114.8 | 137.2 | 156.1 | 174.3 | 197.4 | 228.2 | 256.9 | 292.6
Derated Current in Air |  | 51.8 | 67.2 | 81.9 | 99.4 | 125.3 | 154.7 | 179.9 | 204.4 | 235.9 | 279.3 | 318.5 | 371
Resistance @ 90 degrees in ohm/Km |  | 2.44 | 1.54 | 1.11 | 0.82 | 0.567 | 0.41 | 0.324 | 0.264 | 0.21 | 0.16 | 0.128 | 0.1
Reactance @ 50HZ in ohm/Km |  | 0.0808 | 0.0805 | 0.0783 | 0.075 | 0.074 | 0.0724 | 0.0712 | 0.0716 | 0.0718 | 0.071 | 0.0705 | 0.0704
No.of amps need to carry on each phase (Amp) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No.of meters for run (Mtrs) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No.of runs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Operating Voltage | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415
Voltage drop of cable |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Voltage drop of cable% |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
If feasable in Ground | 2% | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
If feasable in Air |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
0 | Amps
30
If feasable in Ground | #DIV/0! | Sqmm.
If feasable in Air | #DIV/0! | Sqmm.
Al. CABLE CAPACITY(3.5Core) in Sq.mm |  | 16 | 25 | 35 | 50 | 70 | 95 | 120 | 150 | 185 | 240 | 300 | 400
|  | 3x 16+16 | 3x25+16 | 3x35+16 | 3x50+25 | 3x70+35 | 3x95+50 | 3x120+70 | 3x150+70 | 3x185+95 | 3x240+120 | 3x300+150 | 3x400+185
Cable Amps in Al. Cond. Run in Ground |  | 74 | 94 | 113 | 133 | 164 | 196 | 223 | 249 | 282 | 326 | 367 | 418
Cable Amps in Al. Cond. Run in Air |  | 74 | 96 | 117 | 142 | 179 | 221 | 257 | 292 | 337 | 399 | 455 | 530
Total Derating factorb (K1*K2*K3*K4*K5*K6*K7) | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
Derated Current in Ground |  | 51.8 | 65.8 | 79.1 | 93.1 | 114.8 | 137.2 | 156.1 | 174.3 | 197.4 | 228.2 | 256.9 | 292.6
Derated Current in Air |  | 51.8 | 67.2 | 81.9 | 99.4 | 125.3 | 154.7 | 179.9 | 204.4 | 235.9 | 279.3 | 318.5 | 371
Resistance @ 90 degrees in ohm/Km |  | 2.44 | 1.54 | 1.11 | 0.82 | 0.567 | 0.41 | 0.324 | 0.264 | 0.21 | 0.16 | 0.128 | 0.1
Reactance @ 50HZ in ohm/Km |  | 0.0808 | 0.0805 | 0.0783 | 0.075 | 0.074 | 0.0724 | 0.0712 | 0.0716 | 0.0718 | 0.071 | 0.0705 | 0.0704
No.of amps need to carry on each phase (Amp) | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
No.of meters for run (Mtrs) | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
No.of runs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Operating Voltage | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415
Voltage drop of cable |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Voltage drop of cable% |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
If feasable in Ground | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
If feasable in Air |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | Amps
30
If feasable in Ground | #REF! | Sqmm.
If feasable in Air | #REF! | Sqmm.
Al. CABLE CAPACITY(3.5Core) in Sq.mm |  | 16 | 25 | 35 | 50 | 70 | 95 | 120 | 150 | 185 | 240 | 300 | 400
|  | 3x 16+16 | 3x25+16 | 3x35+16 | 3x50+25 | 3x70+35 | 3x95+50 | 3x120+70 | 3x150+70 | 3x185+95 | 3x240+120 | 3x300+150 | 3x400+185
Cable Amps in Al. Cond. Run in Ground |  | 74 | 94 | 113 | 133 | 164 | 196 | 223 | 249 | 282 | 326 | 367 | 418
Cable Amps in Al. Cond. Run in Air |  | 74 | 96 | 117 | 142 | 179 | 221 | 257 | 292 | 337 | 399 | 455 | 530
Total Derating factorb (K1*K2*K3*K4*K5*K6*K7) | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
Derated Current in Ground |  | 51.8 | 65.8 | 79.1 | 93.1 | 114.8 | 137.2 | 156.1 | 174.3 | 197.4 | 228.2 | 256.9 | 292.6
Derated Current in Air |  | 51.8 | 67.2 | 81.9 | 99.4 | 125.3 | 154.7 | 179.9 | 204.4 | 235.9 | 279.3 | 318.5 | 371
Resistance @ 90 degrees in ohm/Km |  | 2.44 | 1.54 | 1.11 | 0.82 | 0.567 | 0.41 | 0.324 | 0.264 | 0.21 | 0.16 | 0.128 | 0.1
Reactance @ 50HZ in ohm/Km |  | 0.0808 | 0.0805 | 0.0783 | 0.075 | 0.074 | 0.0724 | 0.0712 | 0.0716 | 0.0718 | 0.071 | 0.0705 | 0.0704
No.of amps need to carry on each phase (Amp) | 196.8297 | 196.8297 | 196.8297 | 196.8297 | 196.8297 | 196.8297 | 196.8297 | 196.8297 | 196.8297 | 196.8297 | 196.8297 | 196.8297 | 196.8297
No.of meters for run (Mtrs) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
No.of runs | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Operating Voltage | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415
Voltage drop of cable |  | 20.7955 | 13.125 | 9.4602 | 6.9886 | 4.8324 | 3.4943 | 2.7614 | 2.25 | 1.7898 | 1.3636 | 1.0909 | 0.85227
Voltage drop of cable% |  | 5.011% | 3.163% | 2.28% | 1.684% | 1.164% | 0.842% | 0.6654% | 0.5422% | 0.4313% | 0.3286% | 0.2629% | 0.2054%
If feasable in Ground | 2% | FAIL | FAIL | FAIL | FAIL | FAIL | FAIL | FAIL | FAIL | FAIL | FAIL | PASS | PASS
If feasable in Air |  | FAIL | FAIL | FAIL | FAIL | FAIL | FAIL | FAIL | FAIL | FAIL | PASS | PASS | PASS
196.8297 | Amps
30
If feasable in Ground | 300 | Sqmm.
If feasable in Air | 240 | Sqmm.

## Bidcell BOM (LTS)
| Fourth Partner Energy Pvt Ltd | [5 empty] | DOC. No: 4PEL/DES-BCB/662 #I01, R00.
Issue Date: 23/02/2026.
Control Copy No. 02.
BID Cell BOM
SALES BOM (415V LT Level)
Sales BOM Summary |  |  |  | Client Name |  | West Pioneer Properties
Module & Inverters | 19.4981 | per Wp |  | Plant Type (Capex/Opex) |  | Capex
ACCB Panel, DCDB, Optimazer & Spare feeder | 0.85972 | per Wp |  | State Name |  | Maharashtra
Module Mounting Structure | 14.72 | per Wp |  | Shed |  | 0
DC, AC, Control & Communication Cables | 2.74 | per Wp |  | Long Rail |  | 0
Earthing & LA, RMS and BOS | 1.6775 | per Wp |  | RCC |  | 0
Rooftop Infra. (Walkways, cable tray, Ladder & Etc.) | 2.6452 | per Wp |  | RCC Raised |  | 400.52
Ground Infra. (Fencing & Plant lighting) | 0 | per Wp |  | RCC Raised on Pillars |  | 0
I&C and Civil works, Spare & Additional Requirements | -14.1475 | per Wp |  | Ground Mounted |  | 0
Liaisoning, Net metering | 3.725 | per Wp |  | Parking- Car/Bike |  | 0
AMC & Module cleaning | 0 | per Wp |  | Parking-Truck/Bus |  | 0
Total summary break-up |  |  |  | Floating |  | 0
Plant Cost (Total-A) | 27.993 | per Wp |  | Total Plant Capacity |  | 400.52
Plant Cost (Total-A ) without Module | 9.993 | per Wp |  | RFP/RFQ Details
Plant Cost (Total-B) | 31.718 | per Wp |  | Availability of RFP/RFQ |  | Yes
Selling Cost Excluding of GST (For Capex) | 35.2423 | per Wp |  | Is Design According RFP/RFQ |  | Yes
Selling Cost Including of GST (For Opex) | 38.3788 | per Wp |  | Is BOM According To RFP/RFQ |  | No-As per 4PEL Std
Approvals | Name |  | Date of Review/Approval |  | Version no. | Reason for Revision
Sale BOM Reviewed By | Sankar |  | 2026-05-22 |  | V1 | Initial
Sale BOM Approved By | Sankar |  | 2026-05-22
Bidcell BOM Cost valid for 7 days from the date of Approval
Name of the Item's | Unit Cost | Qty | UOM | Total Cost | per Wp | Item's Spec./Scope of Works | Suggested Makes | Remarks/Marketing Comment
SPV Module
Solar Photovoltaic Module | 18 | 400.52 | kWp | 7209360 | 18 | Indian ALMM - Renewsys 620 Wp | Renewsys
Total Cost for PV Module |  |  |  | 7209360 | 18
String Inverters
String Inverter Model | 300000 | 2 | No's | 600000 | 1.4981 | Solis 150 kW | Solis
String Inverter Model | 290000 | 0 | No's | 0 | 0
String Inverter Model | 255000 | 0 | No's | 0 | 0
String Inverter Model | 135000 | 0 | No's | 0 | 0
String Inverter Model | 125000 | 0 | No's | 0 | 0
String Inverter Model | 95000 | 0 | No's | 0 | 0
String Inverter Model | 85000 | 0 | No's | 0 | 0
String Inverter Model | 70000 | 0 | No's | 0 | 0
String Inverter Model | 69000 | 0 | No's | 0 | 0
String Inverter Model | 75000 | 0 | No's | 0 | 0
Inverter extension warranty (6-10 yrars) | 150000 | 1 | No's | FALSE | 0 | No
Total Cost for String Inverters |  |  |  | 600000 | 1.4981
Module Mounting Stucture (MMS) with Hardware
Module Mounting Structure Lord type | #N/A | 0 | No's | 0 | 0 |  | 120mm Short Profile with make of SMS/MTE/Suncon/RPK/sunrack | Profiles selected as per Designer inputs
Module Mounting Structure Standing seam type | #N/A | 0 | No's | 0 | 0 |  |  | #VALUE!
Mid and end Clamp with Hardware | 31 | 0 | No's | 0 | 0
Long Rail Type (Rooftop) with hardware | 2500 | 0 | kWp | 0 | 0 | 100mm Clearance
RCC type (Rooftop) with hardware | 110 | 0 | Tons | 0 | 0 | Fixed Tilt with 500mm Ground Clearance | FPEL- Std. HDG /GI (min. 80 mic thick)with 180kmph (Steel-TATA, JSW,Jindal) (Tubes -Appolo)
RCC Raised Structure type (Rooftop) with hardware | 140 | 40.052 | Tons | 5607280 | 14 | Anchoring with 3000mm Ground Clearance
RCC Raised on Pillar Structure type with hardware | 120 | 0 | Tons | 0 | 0
Ground Mounting type with hardware | 97 | 0 | Tons | 0 | 0 | Fixed Tilt with 500mm Ground Clearance
Ground Raised Structure type (Car/ Bike Parking) | 140 | 0 | Tons | 0 | 0 | J Bold Mounting with 3000mm Ground Clearance
Ground Raised Structure type (Bus/Truck Parking) | 120 | 0 | Tons | 0 | 0 | J Bold Mounting with 6000mm Ground Clearance
Floating Structure Along with cable Trays | 10000 | 0 | kWp | 0 | 0 |  | Reputed make
Hardware for RCC/RCC Raised/ Ground mounted/ Parking | 240 | 1.2016 | Tons | 288374.4 | 0.72 |  | Reputed make
Total Cost for Module Mounting Stucture (MMS) with Hardware |  |  |  | 5895654.4 | 14.72
Junction BOX, DCBD & Optimizers
DCDB with Fuse & SPD | 120000 | 2 | No's | 0 | 0 | Only for Solar edge inverter model | Solar Edge
ACDB with Breaker & SPD | 85000 | 2 | No's | 0 | 0 | Only for Solar edge inverter model
Optimizers for Solar Edge Inverter | 3650 | 323 | No's | 0 | 0 | Optimizers- Model-S 1400/ S 1500
DC/AC side fuse with SPD only for Kerala site's | 63000 | 2 | No's | 0 | 0 | Applicable only on Kerala state | IP 65 Box of DCDB & ACJB
ACJB for below 50kw Inverter | 3500 | 0 | No's | 0 | 0 | For Below 50KW Solis inverters | IP 65 Box with Cu.busbar
Total Cost for Junction BOX, DCBD & Optimizers |  |  |  | 0 | 0
ACCB Panel & Spare Feeder
Total cost of Spare Feeder Along with Al.Bus Bar Extension | 381600 | 0 | Lot | 0 | 0 | 2 Set's of Spare Feeder Extention | Breakers- ABB/ Schneider/ Equilent and Panel from Sri Venkateswara Power Systems/Bhagyashree/ Accupanels/ JVS/Alnico/ DB electrical
Total cost of ACCB Panel at Plant End | 344336 | 1 | Lot | 344336 | 0.85972 | 2 Set's of ACCB Panels
NVR/UVR Panel (Applicable only on Gujarat state) | 37092 | 0 | Lot | 0 | 0 | 2 Set's of NVR or UVR Panels
Contactor/ ACCB Panel(Applicable only on Andhra Pradesh state) | 74000 | 0 | Lot | 0 | 0 | 2 Set's of Contractor or ACB Panels
Isolation Panel | 0 | 0 | No's | 0 | 0
Total Cost for ACCB Panel & Spare Feeder |  |  |  | 344336 | 0.85972
1000V/1500V DC Cu.Cable
1CX4 Sqmm DC solar cable 1.8kV XLPO | 57 | 4050 | Mtr's | 230850 | 0.57638 | 2025 Mtrs Positive & 2025 Mtrs Negative | Siechem
1CX6 Sqmm DC solar cable 1.8kV XLPO | 78 | 0 | Mtr's | 0 | 0 | 0 Mtrs Positive & 0 Mtrs Negative
Total Cost for 1000V/1500V DC Cu.Cable |  |  |  | 230850 | 0.57638
AC Cu. Cable from Inv. to ACJB for below 50kw inverters
4CX16Sqmm Cu. XLPE Copper Un- Armoured Cable-1.1kV | 1168 | 0 | Mtr's | 0 | 0 | 0 Run's of cables with 2 mtrs each on inverters | Polycab/ Equilent
3.5CX25Sqmm Cu. XLPE Copper Un- Armoured Cable-1.1kV | 2336 | 0 | Mtr's | 0 | 0 | 0 Run's of cables with 2 mtrs each on inverters
Total Cost for Cu. Cable from Inv. to ACJB for below 50kw inverter |  |  |  | 0 | 0
AC AL. XLPE Cable from Inv. to ACCB Panel
4CX16Sqmm XLPE Al. Armoured Cable-1.1kV | 176.08 | 0 | Mtr's | 0 | 0 | 0 Run's | Polycab/ Equilent
3.5CX25Sqmm XLPE Al. Armoured Cable -1.1kV | 194.06 | 0 | Mtr's | 0 | 0 | 0 Run's
3.5CX35Sqmm XLPE Al. Armoured Cable -1.1kV | 250.79 | 0 | Mtr's | 0 | 0 | 0 Run's
3.5CX50Sqmm XLPE Al. Armoured Cable -1.1kV | 334.18 | 0 | Mtr's | 0 | 0 | 0 Run's
3.5CX70Sqmm XLPE Al. Armoured Cable -1.1kV | 455.39 | 0 | Mtr's | 0 | 0 | 0 Run's
3.5CX95Sqmm XLPE Al. Armoured Cable -1.1kV | 576.6 | 0 | Mtr's | 0 | 0 | 0 Run's
3.5CX120Sqmm XLPE Al. Armoured Cable -1.1kV | 722.92 | 0 | Mtr's | 0 | 0 | 0 Run's
3.5CX150Sqmm XLPE Al. Armoured Cable -1.1kV | 843.2 | 0 | Mtr's | 0 | 0 | 0 Run's
3.5CX185Sqmm XLPE Al. Armoured Cable -1.1kV | 1066.71 | 0 | Mtr's | 0 | 0 | 0 Run's
3.5CX240Sqmm XLPE Al. Armoured Cable -1.1kV | 1359.66 | 0 | Mtr's | 0 | 0 | 0 Run's
3.5CX300Sqmm XLPE Al. Armoured Cable -1.1kV | 1686.4 | 20 | Mtr's | 33728 | 0.084211 | 2 Run's
Total Cost for AL. XLPE Cable from Inv. to ACCB Panel |  |  |  | 33728 | 0.084211
AC Al.cable From ACCB Panel to Client Termination
4CX16Sqmm XLPE AC Al. Armoured Cable-1.1kV | 176.08 | 0 | Mtr's | 0 | 0 | 0 Run's | Polycab/ Equilent
3.5CX25Sqmm XLPE Al. Armoured Cable -1.1kV | 194.06 | 0 | Mtr's | 0 | 0 | 0 Run's
3.5CX35Sqmm XLPE Al. Armoured Cable -1.1kV | 250.79 | 0 | Mtr's | 0 | 0 | 0 Run's
3.5CX50Sqmm XLPE Al. Armoured Cable -1.1kV | 334.18 | 0 | Mtr's | 0 | 0 | 0 Run's
3.5CX70Sqmm XLPE Al. Armoured Cable -1.1kV | 455.39 | 0 | Mtr's | 0 | 0 | 0 Run's
3.5CX95Sqmm XLPE Al. Armoured Cable -1.1kV | 576.6 | 0 | Mtr's | 0 | 0 | 0 Run's
3.5CX120Sqmm XLPE Al. Armoured Cable -1.1kV | 722.92 | 0 | Mtr's | 0 | 0 | 0 Run's
3.5CX150Sqmm XLPE Al. Armoured Cable -1.1kV | 843.2 | 0 | Mtr's | 0 | 0 | 0 Run's
3.5CX185Sqmm XLPE Al. Armoured Cable -1.1kV | 1066.71 | 440 | Mtr's | 469352.4 | 1.1719 | 2 Run's
3.5CX240Sqmm XLPE Al. Armoured Cable -1.1kV | 1359.66 | 0 | Mtr's | 0 | 0 | 0 Run's
3.5CX300Sqmm XLPE Al. Armoured Cable -1.1kV | 1686.4 | 170 | Mtr's | 286688 | 0.71579 | 1 Run's
Total Cost for AL.XLPE Cable from LT Panel to client Termination |  |  |  | 756040.4 | 1.8876
Earthing, Power supply & Communication Cables
1Cx4sqmm cable for Module Frame earthing | 62.54 | 135.66 | Mtr's | 8484.1764 | 0.021183 | 646 no. of Modules with 200 mm cut length cable | Polycab/ Equilent
1Cx16sqmm Inverter Earthing | 398.56 | 0 | Mtr's | 0 | 0 | 0 Run's of cables with 2 mtrs on each inverters |  |  |  |  | TN 38 DQ 2683 | TN 38 CK 2698
1Cx25sqmm Inverter Earthing | 590.42 | 0 | Mtr's | 0 | 0 | 0 Run's of cables with 2 mtrs on each inverters |  |  |  |  | 4538412683 | 4538322698
1Cx35sqmm Inverter Earthing | 801.36 | 0 | Mtr's | 0 | 0 | 0 Run's of cables with 2 mtrs on each inverters |  |  |  |  | 44 | 50
1CX50sqmm for LA Earthing & Inverter Earthing | 1082.26 | 0 | Mtr's | 0 | 0 | 0 Run's of cables with 2 mtrs on each inverters |  |  |  |  | 8 | 5
1CX70sqmm for LA Earthing & Inverter Earthing | 1520.04 | 19 | Mtr's | 28880.76 | 0.072108 | 2 Run's with 2 mtrs each inv. & 1 no. of LA with 20 Mtrs each
10CX2.5sqmm for DGPD & ZFD | 417.64 | 25 | Mtr's | 10441 | 0.026069 | 1 Run's of cables with 25 mtrs each on ZFD & DGPD |  |  |  |  | 4 | 4
3CX2.5sqmm for motor wiring | 120.84 | 90 | Mtr's | 10875.6 | 0.027154 | 2 Run's of cables with 45 mtrs on each 1HP Water Pump |  |  |  |  | 5 | 5
5CX2.5sqmm for motor wiring | 206.7 | 0 | Mtr's | 0 | 0 | 0 Run's of cables with 45 mtrs each on Booster Pump |  |  |  |  | 3 | 3
Communication cable RS 485 cable 2Px2Px0.5sqmm | 159 | 70 | Mtr's | 11130 | 0.027789 | 2 no. of Inverters with 10 mtr's lenthg each |  |  |  |  | 8 | 8
Cat-6 cable for wattmon wiring | 34.98 | 200 | Mtr's | 6996 | 0.017467 | 2 no. of ACCB Panel with 100 mtrs length each |  |  |  |  | 4 | 3
4Cx16sqmm Al. Ar. XLPE Cable-(LV Wiring of for periphery) | 176.08 | 50 | Mtr's | 0 | 0 | 4Cx16sqmm Al. Cable Multicolour |  |  |  |  | 1 | 2
Total Cost for Earthing, Power supply & Communication Cables |  |  |  | 76807.5364 | 0.19177 | [5 empty] | 2 | 2
Chemical Earthing & Lighting Arrester (LA) | [10 empty] | 6 | 6
Early Streamer Emmision LA- 107m Radius | 20000 | 1 | No's | 20000 | 0.049935 | 1 no. LA 107m radius without Counter | LPI/ Equilent |  |  |  | 8 | 9
Air Lighting Terminal LA's | 535185.1852 | 0 | Set's | 0 | 0 | Air Lighting Terminal | Reputed make |  |  |  | 3 | 8
GI Earthing electrode | 1400 | 13 | No's | 18200 | 0.045441 | 3 mtrs GI Earthing Electrode | Indelec/ Equilent |  |  |  | 44 | 50
Earthpit chamber cover | 1850 | 13 | No's | 24050 | 0.060047 | 13 no. of 2 feet x 2 feet size GI Earthpit Chember cover | Reputed make |  |  |  | 8
Bentonite powder | 550 | 26 | Pakage | 14300 | 0.035704 | 26 no. of Pakage with 25kg each | Indelec/ Equilent
25X3mm GI Earth strip | 80 | 614.4 | kg's | 49152 | 0.12272 | per mtr is equal to 0.6 kg's | GI/HDG/ Equilent
25X6mm GI Earth strip | 75 | 141.6 | kg's | 10620 | 0.026516 | per mtr is equal to 1.18 kg's
40X6mm GI Earth strip | 75 | 0 | kg's | 0 | 0 | per mtr is equal to 2 kg's
50X6mm GI Earth strip | 75 | 0 | kg's | 0 | 0 | per mtr is equal to 2.34 kg's
Total Cost for Chemical Earthing & Lighting Arrester (LA) |  |  |  | 136322 | 0.34036
Walkways
Walkways | 420 | 350 | Mtr's | 147000 | 0.36702 | L:1000xW:300xT:25 mm | FRP
Step Walkways width size 500mm | 462 | 0 | Mtr's | 0 | 0
Zero degree Walkways with size 300 mm | 420 | 0 | Mtr's | 0 | 0
Total Cost for Walkways |  |  |  | 147000 | 0.36702
DC Cable Tray
Cable Trays from Module to Inverter for Rooftop | 365 | 350 | Mtr's | 127750 | 0.31896 | 50x50x2mm | FRP
| 339.19 | 0 | Mtr's | 0 | 0 | 100x50x2mm
Total Cost for DC Cable Tray |  |  |  | 127750 | 0.31896
AC Cable Tray from Inverter to ACCB Panel
100x75x2mm ladder Type Cable Tray | 332.64 | 20 | Mtr's | 6652.8 | 0.01661 | GI/HDG/ Powder coated material Ladder type cable trays | GI
150x75x2mm ladder Type Cable Tray | 349.92 | 0 | Mtr's | 0 | 0
200x75x2mm ladder Type Cable Tray | 368.28 | 0 | Mtr's | 0 | 0
300X75X2mm Ladder Type Cable Tray | 403.92 | 0 | Mtr's | 0 | 0
400X75X2mm Ladder Type Cable Tray | 439.56 | 0 | Mtr's | 0 | 0
500X75X2mm Ladder Type Cable Tray | 475.2 | 0 | Mtr's | 0 | 0
600x75x2mm Ladder Type Cable Tray | 510.84 | 0 | Mtr's | 0 | 0
Total Cost for AC Cable Tray from Inverter to ACCB Panel |  |  |  | 6652.8 | 0.01661
AC Cable Tray from ACCB Panel to Client LT Panel
100x75x2mm ladder Type Cable Tray | 332.64 | 170 | Mtr's | 56548.8 | 0.14119 | GI/HDG/ Powder coated material Ladder type cable trays | GI
150x75x2mm ladder Type Cable Tray | 349.92 | 0 | Mtr's | 0 | 0
200x75x2mm ladder Type Cable Tray | 368.28 | 220 | Mtr's | 81021.6 | 0.20229
300X75X2mm Ladder Type Cable Tray | 403.92 | 0 | Mtr's | 0 | 0
400X75X2mm Ladder Type Cable Tray | 439.56 | 0 | Mtr's | 0 | 0
500X75X2mm Ladder Type Cable Tray | 475.2 | 0 | Mtr's | 0 | 0
600x75x2mm Ladder Type Cable Tray | 510.84 | 0 | Mtr's | 0 | 0
Total Cost for AC Cable Tray from ACCB Panel to Client LT Panel |  |  |  | 137570.4 | 0.34348
Roof Access & Rooftop Accessories
Monkey Ladder for Roof Access | 13500 | 0 | Mtr's | 0 | 0 | Client Scope | HDG mesh type material with Installation BOQ.
Staircase-Step ladder for Roof Access | 65500 | 0 | Mtr's | 0 | 0
Movable Ladder for Parking structures | 50000 | 1 | No's | 50000 | 0.12484 | 1 No's of Movable ladder considered
Roof monitor cross over | 95000 | 0 | No's | 0 | 0 | 0 No's Considered as per designer input
Ladder for Roof to Roof | 10000 | 0 | Mtr's | 0 | 0 | 0 Mtr's Considered as per designer input
Railings on Roof Edge's with toe guard - 1 Mtr Height | 970 | 0 | Mtr's | 0 | 0 | Consider Railings for Module tilt >=8 | HDG
Mesh Over the Skylight width <600mm | 1033 | 0 | Rmtr's | 0 | 0 | Not Required | GI/ Equilent
Mesh Over the Skylight width 600-1200mm | 1133 | 0 | Rmtr's | 0 | 0
Mesh Over the Skylight width 1200-1700mm | 2000 | 0 | Rmtr's | 0 | 0
Mesh Over the Skylight width 1700-2200mm | 2600 | 0 | Rmtr's | 0 | 0
Turbo Vent Mesh | 3500 | 0 | No's | 0 | 0 | Not Applicable
Lifeline (Rope & Acc. ) Along with Installion charge | 1100 | 350 | Mtr's | 385000 | 0.96125 | Lifegear safetech private limited | Karam/Lifegear/Omkar Safety and Power Pvt Ltd/ Equilent
Lifeline (Post) Along with Installion charge | 3546 | 51 | No's | 180846 | 0.45153
Runner > Removable runner made of SS 316 | 3080 | 8 | No's | 24640 | 0.06152
Vertical Lifeline for Monkey ladder | 3250 | 0 | Mtrs | 0 | 0 | 0 Mtr's Considered as per ladder Height
Gutter length for Cleaning / Rain water harvesting | 2500 | 0 | Mtr's | 0 | 0 | Not Required | Reputed make
Gutters Dropdown for every 10 mtrs length | 3500 | 0 | No's | 0 | 0 |  | Reputed make
Total Cost for Roof Access & Rooftop Accessories |  |  |  | 640486 | 1.5991
Remote Monitoring & Weather Monitoring
Remote monitoring system by using 4PEL server | 25000 | 2 | No's | 50000 | 0.12484 | 2 Nos. of Online monitoring | Wattmon / Equilent
SCADA Cloud based/ PLC based | 1000000 | 0 | No's | 0 | 0 | Cloud Based | 4PEL Make
Irradiation sensor | 28000 | 1 | No's | 28000 | 0.069909 |  | Surya Logics/Any Reputed Make
Pyranometer Horizontal | 0 | 0 | No's | 0 | 0 |  | Kipp & Zonen/ Equilent
Pyranometer Module tilted | 0 | 0 | No's | 0 | 0
Module Temperature Sensor | 29000 | 0 | No's | 0 | 0 | To Measure the module Temperature | Surya Logics/Any Reputed Make
Ambient Temperature Sensor | 26000 | 0 | No's | 0 | 0 | To Measure the external temperature
Anemometer | 20000 | 0 | No's | 0 | 0 | To Measure the wind speed
Rain gauge Sensor | 20000 | 0 | No's | 0 | 0 | To Measure rainfall
Weather Station Tripod Mounting Stand with junction box | 27500 | 0 | No's | 0 | 0 | Mounting Stand
Data Logger | 25000 | 0 | No's | 0 | 0
Humidity Sensor | 13250 | 0 | No's | 0 | 0 | To Measures the Moisture and Air Temperature
Zero Feeding device for LT (If NO Netmetering) | 45000 | 0 | No's | 0 | 0 | Net Metering/Net Billing | Wattmon / Equilent
DG Protection device for LT supply | 45000 | 1 | No's | 45000 | 0.11235 | DG Protection Device by Using Wattmon
Total Cost for Remote Monitoring & Weather Monitoring |  |  |  | 123000 | 0.3071
Plant Fancing with Lighting works
Boundary wall alongwith protection on top (6 ft's) | 0 | FALSE | Mtr's | 0 | 0 | 0 | Reputed make
Main Gate | 50000 | 0 | No's | 0 | 0 | 0 | Reputed make
Pole (Min. 5.4 meter pole HDG lighting Pole) | 5000 | 0 | No's | 0 | 0 | 0 | Reputed make
Street Light (20 Watts LED with Enclosure IP65,JB & Cable) | 6000 | 0 | No's | 0 | 0 |  | CG/Philips/ Equilent make
Total Cost for Plant Fancing with Lighting works |  |  |  | 0 | 0
Balance of System (BOS)
Rooftop BOM Item's
Lord Chemical-400ML Catridge 810 for MMS | 2500 | 0 | No's | 0 | 0 | for MMS | Parker- Lord
Lord Chemical-400ML Catridge 810 for Others | 2500 | 0 | No's | 0 | 0 | for Walkways,DC cable trays & Skylight mesh
Earth Strip Clamps | 6 | 615 | No's | 3690 | 0.009213 |  | Reputed make
M8X25 Self triding screw and wooden Gutties | 3.5 | 3179.6 | No's | 11128.6 | 0.027785 |  | STR/SANA/ Equilent
M8x25mm for Earth Strip and cable tray | 6.5 | 542 | No's | 3523 | 0.0087961
Base clamp 100mm | 35 | 370 | No's | 12950 | 0.032333 |  | Reputed make
Base clamp 200mm | 70 | 0 | No's | 0 | 0 |  | Reputed make
Base clamp 300mm | 120 | 0 | No's | 0 | 0 |  | Reputed make
M-clamp SS - Walkway clamps | 17 | 1176 | No's | 19992 | 0.049915 |  | Reputed make
SSP 1045 Profile 75mm for lord type inst. | 54 | 1528 | No's | 0 | 0 | Walkway and skylight mesh only for Lord fixing | SMS/Equilent
SSP 5 - 50mm for Sanding seam or Kliplock type | 65 | 1528 | No's | 0 | 0 | Walkway and skylight mesh only for standing seam fixing
M8x15mm Walkway jointer with hardware | 25 | 245.7 | No's | 6142.5 | 0.015336 |  | FLU-con/Tibro
Step and Zero degree walkway Supports GI raised Leg | 170 | 0 | No's | 0 | 0 |  | Reputed make
Bus Insulators for LA strip | 35 | 0 | No's | 0 | 0 |  | Reputed make
32mm Flexible Pipe used for module to cable Tray | 95 | 45 | Mtr's | 4275 | 0.010674 |  | Elettro/ Equilent
Common BOS Item's
Industrial wall socket box with MCB (Single phase two pole) | 830 | 2 | No's | 1660 | 0.0041446 | Industrial wall socket box with MCB | Exora/ Equilent
Industrial wall socket box with MCB (Three phase four pole) | 1850 | 0 | No's | 0 | 0 | Industrial wall socket box with MCB | Exora/ Equilent
Module water drainage clips | 20 | 1292 | No's | 25840 | 0.064516 | For Module tilt < 5, other than shed | Reputed make
Module water drainage clips | 20 | 0 | No's | 0 | 0 | For Module tilt < 8, for shed | Reputed make
Cable Ties -Nylon 150mm | 50 | 7 | Packet's | 350 | 0.00087386 |  | FLU-con/Tibro/ Equilent
Cable Ties -Nylon 200mm | 60 | 6 | Packet's | 360 | 0.00089883
Cable Ties -Nylon 300mm | 290 | 6 | Packet's | 1740 | 0.0043444
Cable Ties -Nylon 450mm | 330 | 6 | Packet's | 1980 | 0.0049436
Cable Ties -SS 200mm | 540 | 6 | Packet's | 3240 | 0.0080895
Cable Ties -SS 300mm | 700 | 6 | Packet's | 4200 | 0.010486
Cable Ties -SS 500mm | 860 | 6 | Packet's | 5160 | 0.012883
LA support- 5 mtrs GI pipe | 1850 | 1 | No's | 1850 | 0.004619 |  | Reputed make
Stay wires for LA | 25 | 25 | Mtr's | 625 | 0.0015605 |  | Reputed make
MC4 connector Male and Female | 52 | 170 | No's | 8840 | 0.022071 |  | Elmex/ Equilent
Inline Fuse Male & Female | 650 | 33 | No's | 21450 | 0.053555
DC cable dressing clips | 6 | 1421.2 | No's | 8527.2 | 0.02129 |  | Araymond/ Equilent
Fire extinguisher CO2 | 5000 | 2 | No's | 10000 | 0.024968 |  | Safe Pro Fire Services Pvt Ltd
Fire extinguisher ABC type | 5000 | 2 | No's | 10000 | 0.024968
Fire Bucket with Stand and canopy | 4200 | 2 | No's | 8400 | 0.020973 |  | Reputed make
Conduit pipe fixing(joining) Solvent (1000 ml) | 1000 | 2 | No's | 2000 | 0.0049935 |  | Birla/ Equilent
Pu sealant for closing the opening of the pipes/conduits | 500 | 7 | No's | 3500 | 0.0087386 |  | ABRO Industries/ Reputed make
Sleeves each colour 250mm length Inv. To ACCB panel | 150 | 2 | Mtr's | 300 | 0.00074903 |  | WOER Tube/ Equilent
Sleeves each colour 250mm ACCB panel to Termination | 200 | 4 | Mtr's | 800 | 0.0019974
Insulation PVC Tape (R, Y, B, B, G) | 40 | 10 | No's | 400 | 0.0009987 |  | ABRO/Biocon/Equilent
Ferrules | 150 | 4 | No's | 600 | 0.0014981 |  | Reputed make
M4x20mm for module frame earthing | 3 | 1421.2 | No's | 4263.6 | 0.010645 |  | FLU-con/Tibro/ Equilent
M8x15mm for walkways | 4 | 1176 | No's | 4704 | 0.011745
Hose pipe for water | 85 | 80 | Mtr's | 6800 | 0.016978 |  | Champion (Savera)/Equilent
25 mm CPVC Pipe for Water piping & array looping purpose | 110 | 504 | Mtr's | 55440 | 0.13842 |  | Birla/ Equilent
25 mm CPVC T-bend | 32 | 60.48 | No's | 1935.36 | 0.0048321
25 mm CPVC L-bend | 28 | 60.48 | No's | 1693.44 | 0.0042281
25 mm CPVC Ball value | 215 | 23.46 | No's | 5043.9 | 0.012593
25 mm CPVC Coupler | 18 | 168 | No's | 3024 | 0.0075502
CVPC Solution 934ml | 980 | 4 | No's | 3920 | 0.0097873
CPVC Pipe C Clamp | 10 | 529.2 | No's | 5292 | 0.013213
CPVC Pipe End cap | 15 | 6 | No's | 90 | 0.00022471
25mm CPVC MTA and FTA | 60 | 4 | No's | 240 | 0.00059922
25mm CPVC Union | 95 | 4 | No's | 380 | 0.00094877
600 KVA UPS | 2500 | 2 | No's | 5000 | 0.012484 |  | i-Ball/ Equilent
Communication SPD one for wattman & Irradiation Sensor | 3000 | 3 | No's | 9000 | 0.022471 |  | Citel/ Equilent
Earthing name plates | 210 | 13 | No's | 2730 | 0.0068161 |  | Reputed make
Danger board AC 415V and DC 1500V | 310 | 4 | No's | 1240 | 0.003096
Fourthpartner Name Plant | 350 | 4 | No's | 1400 | 0.0034955
LT Cable Route marker | 130 | 0 | No's | 0 | 0
Insulation mats 1Mtrx1Mtr for Inverter & ACCB 3.3kv | 1200 | 6 | No's | 7200 | 0.017977
Hume Pipe 300mm Dia | 1400 | 0 | Mtr's | 0 | 0
DWC Pipe for Ground Mounted Type | 42 | 0 | Mtr's | 0 | 0 |  | Nagarjuna polymers / Equilent
DWC Pipe T bend | 35 | 0 | No's | 0 | 0
DWC Pipe L bend | 33 | 0 | No's | 0 | 0
DWC Pipe Coupler | 28 | 0 | No's | 0 | 0
PVC Water Tank 5000 Ltrs | 52000 | 0 | No's | 0 | 0 |  | Sintex/ Equilent
PVC Water Tank 2000 Ltrs | 23500 | 0 | No's | 0 | 0
1 HP Water pump | 4000 | 2 | No's | 8000 | 0.019974 |  | Crompton Greaves/ Equilent
1.5 HP Water pump | 10500 | 0 | No's | 0 | 0 | [7 empty] | 3187080 |  | PL | Total loan amount | Tenure | ROI | EMI | Repayment
Booster Water pump | 25000 | 0 | No's | 0 | 0 | [9 empty] | Old | 2306513 | 54 | 10.9% | 54231 | 2928474
Water flow meter | 6400 | 2 | No's | 12800 | 0.031958 |  | Kranti/ Equilent | [7 empty] | New | 2520000 | 60 | 10.05% | 53605 | 3216300
Water Pressure release Value | 5500 | 2 | No's | 11000 | 0.027464 |  | Aqua/ Equilent |  |  | 0 |  |  |  |  | New | 200000 | 60 | 10.05% | 4250 | 255000
2.5 Sqmm Cu. & Bimetallic Lug's Pin & Ring type | 10 | 35.2 | No's | 352 | 0.00087886 |  | Dowell's/ Equilent
4 Sqmm Cu. Lug's Round type | 6 | 1421.2 | No's | 8527.2 | 0.02129 |  |  |  |  | 26231 | 0 | 60 | 53605 | 3216300
16 Sqmm Cu. & Bimetallic Lug's Pin & Ring type | 190 | 0 | No's | 0 | 0 | [13 empty] | Old Vs new | 287826
25 Sqmm Cu. & Bimetallic Lug's Pin & Ring type | 45 | 0 | No's | 0 | 0 |  |  |  |  | 54231 | 0 |  | old | 0 |  |  |  |  | 2L add. | 255000
35 Sqmm Cu. & Bimetallic Lug's Pin & Ring type | 145 | 0 | No's | 0 | 0 | [5 empty] | 0 |  | new | 3216274 |  |  |  |  | Diff. | 32826
50 Sqmm Cu. & Bimetallic Lug's Pin & Ring type | 220 | 0 | No's | 0 | 0 | [7 empty] | 4249 | 3216274 |  |  |  |  | service charge | 6000
70 Sqmm Cu. & Bimetallic Lug's Pin & Ring type | 250 | 0 | No's | 0 | 0 |  |  |  |  | 0 |  |  | 254940 | 2961334 |  |  |  |  | additial pay | 38826
16 Sqmm Bimetallic Lug's Pin type | 190 | 0 | No's | 0 | 0 |  |  |  |  | 0 |  |  |  | 2967334
25 Sqmm Bimetallic Lug's Pin type | 45 | 0 | No's | 0 | 0 |  |  |  |  | 0
35 Sqmm Bimetallic Lug's Pin type | 145 | 0 | No's | 0 | 0
50 Sqmm Bimetallic Lug's Pin type | 220 | 0 | No's | 0 | 0 | [6 empty] | 22708.33
70 Sqmm Bimetallic Lug's Pin type | 250 | 0 | No's | 0 | 0 | [6 empty] | 22422 | 286.33
95 Sqmm Bimetallic Lug's Pin type | 260 | 0 | No's | 0 | 0 | [6 empty] | 22133.06 | 288.94
120 Sqmm Bimetallic Lug's Pin type | 295 | 0 | No's | 0 | 0 | [6 empty] | 21841.5 | 291.56
185 Sqmm Bimetallic Lug's Pin type | 505 | 0 | No's | 0 | 0
240 Sqmm Bimetallic Lug's Pin type | 510 | 0 | No's | 0 | 0
300 Sqmm Bimetallic Lug's Pin type | 680 | 0 | No's | 0 | 0
16 Sqmm AL. Lug's Ring type | 7 | 0 | No's | 0 | 0
25 Sqmm AL. Lug's Ring type | 9 | 0 | No's | 0 | 0
35 Sqmm AL. Lug's Ring type | 12 | 0 | No's | 0 | 0
50 Sqmm AL. Lug's Ring type | 15 | 0 | No's | 0 | 0
70 Sqmm AL. Lug's Ring type | 19 | 0 | No's | 0 | 0
95 Sqmm AL. Lug's Ring type | 21 | 0 | No's | 0 | 0
120 Sqmm AL. Lug's Ring type | 31 | 0 | No's | 0 | 0
150 Sqmm AL. Lug's Ring type | 36 | 0 | No's | 0 | 0
185 Sqmm AL. Lug's Ring type | 40 | 17.6 | No's | 704 | 0.0017577
240 Sqmm AL. Lug's Ring type | 62 | 0 | No's | 0 | 0
300 Sqmm AL. Lug's Ring type | 87 | 8.8 | No's | 765.6 | 0.0019115
Freight & Handling By Road | 67500 | 1 | Truck | 67500 | 0.16853 | Hyderabad to Maharashtra | Goods Transportation (Only BOS)
Total Cost for Balance of the System (BOS) |  |  |  | 412568.4 | 1.0301
Spare List for O&M and Plant Insurance of BOS
Spare list cost | 16878125.9364 | 1% | Percentage | 0 | 0 | Not Applicable
Total Plant Insurance for BOS | 1269627.2311 | 0 | Yr's | 0 | 0 | No
Total Cost for Spare List for O&M and Plant Insurance of BOS |  |  |  | 0 | 0
Addinatinal Item's (Requirement) for ITC Sites
Thermography test & Power analyser | 60000 | 0 | No's | 0 | 0 |  | Reputed make
GI Conduit | 56 | 0 | Mtrs | 0 | 0 |  | Reputed make
ABG Making | 150 | 0 | Kwp | 0 | 0 |  | Fourth Partner Energy
Module to Module earthing 6 sqmm cable | 84 | 0 | Mtr's | 0 | 0 |  | Polycab/ Equilent
Load flow ananlysys by ETAP | 150000 | 2 | no's | 0 | 0 |  | Reputed make
Display 43 inch | 50000 | 0 | No's | 0 | 0 |  | Reputed make
Total Cost for Addinatinal Item's (Requirement) for ITC Sites |  |  |  | 0 | 0
Additional Requirements - D mart Sites
Ladder 1.5 mtrs height for RCC type inst. | 15000 | 0 | No's | 0 | 0
Ladder 2.5 mtrs height for Carparking type inst. | 45000 | 0 | No's | 0 | 0
Structure Stability Report | 25000 | 0 | No's | 0 | 0
Total Cost for Addinatinal Item's (Requirement) for Dmart Sites |  |  |  | 0 | 0
Additional Requirements (If any)
Almm | -3000 | 400.52 | No's | -1201560 | -3
MMS | 5895654.4 | -1 | No's | -5895654.4 | -14.72
Net meter | 980000 | -1 | No's | -980000 | -2.4468
|  |  | No's | 0 | 0
| 0 | 0 | No's | 0 | 0
| 0 | 0 | No's | 0 | 0
| 0 | 0 | No's | 0 | 0
Total Cost for Additional Requirements |  |  |  | -8077214.4 | -20.1668
I&C, Project Management & Safety officer
Project Management | 73000 | 2 | Months | 146000 | 0.36453 |  | Fourth Partner Energy
Special Safty Officer While I&C works | 75000 | 0 | Months | 0 | 0
Shed (Rooftop) All Civil & I&C works. | 1550 | 0 | KWp | 0 | 0
Long Rail Type (Rooftop) All Civil & I&C works. | 1850 | 0 | KWp | 0 | 0
RCC (Rooftop) All Civil & I&C works. | 3500 | 0 | KWp | 0 | 0
RCC Raised Structure (Rooftop) All Civil & I&C works. | 5500 | 400.52 | KWp | 2202860 | 5.5
RCC Raised on Pillar Str. type All Civil & I&C works. | 6400 | 0 | KWp | 0 | 0
Ground All Civil & I&C works. | 2500 | 0 | KWp | 0 | 0
GRS (Parking- Car/ Bike)All Civil & I&C works. | 6400 | 0 | KWp | 0 | 0
GRS (Parking- Bus/ Truck)All Civil & I&C works. | 8000 | 0 | KWp | 0 | 0
Floating Structure All Civil & I&C works. | 2800 | 0 | KWp | 0 | 0
Supply & Installation of inverter stand with canopy | 9000 | 2 | No's | 18000 | 0.044942
Supply & Installation of ACCB panel stand with canopy | 44000 | 1 | Lot | 44000 | 0.10986 | 2 Set's of ACCB Panels Stand with canopy
Using Soil Trench( AC Cable From ACCB panel to CLTP) | 400 | 0 | Mtr's | 0 | 0 | Soil Trench
Local Union Labour Charges for Kerala | 800 | 0 | Kwp | 0 | 0 | Applicable for Kerala state
Road Crossing work | 800 | 0 | Mtr's | 0 | 0 | RCC/ Bitamin road Etc.
Cable Gantry | 25000 | 0 | Mtr's | 0 | 0 | 3 mtrs Height Gantry
Ground mounted Plant Civil Works
Soil Test/Pullout Test (for Ground & Car Parking) | 75000 | 0 | Sample | 0 | 0 | 0 | Civil work
Land Leveling (for Ground & Car Parking) | 35000 | 0 | Acres | 0 | 0 | 0
Bathymetry test | 800000 | 0 | Set's | 0 | 0 | 0
Computational Fluid Dynamics (CFD) study | 500000 | 0 | Set's | 0 | 0
Approach Road width- 3.5m with 0.5m shoulders | 1850 | 0 | Mtr's | 0 | 0 | 0
Internal Road 3 mtrs wide with 0.5mtrs shoulders | 1850 | 0 | Mtr's | 0 | 0 | 0
Peripheral road 2.5 mtrs wide with 0.5mtrs shoulders | 1450 | 0 | Mtr's | 0 | 0 | 0
Strom Water Drainage | 1850 | 0 | Mtr's | 0 | 0 | 0
Inverter control room | 850 | 1200 | Sq. ft. | 0 | 0 | Cabin type
Total Cost for I&C, Project Management & Safety officer |  |  |  | 2410860 | 6.0193
No Row Inclusion Beyond This
Total - A |  |  |  | 11211771.5364 | 27.993 | Plant Cost W/O Liaisoning & EPC
[6 empty] | No existing plant | States Vs Net Metering Limit table
CEIG, Discom NOC, Liaisoning & Net Metering
CEIG/ Minister cost | 190000 | 1 | Set's | 190000 | 0.47438 | 4PEL Scope | With Respect to State
NET metering Liaisoning fee NOC | 290000 | 2 | Set's | 580000 | 1.4481 | 4PEL Scope | on AC - 1 MW NM, above BTM
Net metering (ABT Meter) Materials & Installation | 200000 | 2 | Set's | 400000 | 0.9987 | 4PEL Scope | Secure / L&T/Equilent
Statutory Fees | 40000 | 2 | Set's | 80000 | 0.19974 | 4PEL Scope | BTM
Metering Cubicle (CT&PT) with Installtion along Testing Fee | 0 | 2 | Set's | 0 | 0 | Client Scope | Kalpa/Kappa/ Equilent
GOK only applicable for Karnataka | 1121456 | 0 | Set's | 0 | 0 | 4PEL Scope | Only for Karnataka State
Minister cost for tamil nadu state | 900000 | 0 | Set's | 0 | 0 | 4PEL Scope | Only for Tamil nadu State
GEIG & NOC cost for tamil nadu state | 360000 | 0 | Set's | 0 | 0 | 4PEL Scope
Total cost of Generation Panel before client termination | 135000 | 0 | Set's | 0 | 0 | 2 Set's of Generation Panel | Breakers- ABB/ Schneider/ Equilent and Panel from Sri Venkateswara Power Systems/Bhagyashree/ Accupanels/ JVS/Alnico/ DB electrical
Generation Panel with breaker before client termination for MH | 120968 | 2 | Set's | 241936 | 0.60405 | 2 Set's of Generation Panel with breaker
Renewable Purchase Obligation (RPO) | 0 | 1 | MWp | 0 | 0 | Client Scope
RTU Installation for Madhya Pradesh | 800000 | 0 | Set's | 0 | 0 | Applicable only on MP State | Only for MP State
Running Cost for RTU Madhya Pradesh | 150000 | 0 | Yr's | 0 | 0 | Applicable only capex model
DISCOM NOC, Nodal Agency & Grid conn. Approval + Cable | 1050000 | 0 | Set's | 0 | 0 | DISCOM NOC, Nodal Agency & Grid con. Approval NA | Only for AP State
RTU & SLDC Communication System for AP state | 3800000 | 0 | Set's | 0 | 0 | Below 1MW RTU & SLDC Not required
Discom Meter with CT's w.r.t No. of LT panel | 47500 | 2 | No's | 0 | 0 | 4PEL Scope
Total Cost for CEIG, Discom NOC, Liaisoning & Net Metering |  |  |  | 1491936 | 3.725
Total - B |  |  |  | 12703707.5364 | 31.718 | Plant Cost with Liaisoning & W/O EPC
EPC Margin, Marketing Commission
Engineering Procurement and Construction (EPC) Margin | 10% |  |  | 1411523.0596 | 3.5242 | 10% Considered as per BD's Input's | Decided by BD
Marketing or Channel Partner Commission | 0% |  |  | 0 | 0 | 0% of Total-A
Total cost of EPC Margin, Marketing Commission |  |  |  | 1411523.0596 | 3.5242
AMC and Module Cleaning
Annual Maintenance Contract (AMC) & Module Cleaning | 0 | 1 | Yr's | 0 | 0 | 0 | Capex
CAMC for ITC sites | 1000 | 0 | KWp | 0 | 0 | Only for ITC sites
Total Cost for AMC & Module Cleaning |  |  |  | 0 | 0
Total Selling Cost Excluding of GST (For Capex) |  |  |  | 14115230.596 | 35.2423 | Plant Cost w/o GST
Total Cost of BG with Plant Capacity |  |  |  | 0 | 0 | 0% with - Years
Total Selling Cost Including of BG Value |  |  |  | 14115230.596 | 35.2423 | Your Capex Cost is Here
Goods and Services Tax (GST) | 8.9% |  |  | 1256255.523 | 3.1366 | Your GST Cost is Here
Total Selling Cost Including of All GST (For Opex) |  |  |  | 15371486.119 | 38.3788 | Your Opex Cost is Here
End Of Statement ( Best of luck )
[21 empty] | S.No | Name of the state | CEIG Applicability | NM Applicability |  |  |  | Above NM Limit |  | Return value of NM limit
Item's | Cost Exlus.Tax/Wp | % | [21 empty] | DC Capacity |  | AC Capacity
Modules | 18 | 56.75% | [18 empty] | 1 | Andhra Pradesh | Yes | 500 KWp NM, till 1MWp NB |  |  |  | BTM |  | on DC - 500 KWp NM, till 1MWp NB, above BTM
Inverters | 1.4981 | 4.723% | [18 empty] | 2 | Assam | Yes | 500 KWp DC |  |  |  | BTM |  | on DC - 500 KWp NM, above BTM
ACCB Panel, DCDB, Optimazer & Spare feeder | 0.85972 | 2.711% | [18 empty] | 3 | Bihar | >100 KWp | upto 1 MW |  |  |  | Captive |  | on DC - 1 MWp NM, above captive
Module Mounting Structure | 14.72 | 46.41% | [18 empty] | 4 | Chhattisgarh | Yes |  |  | upto 500 kWp NM |  | Captive |  | on AC - 500 KW NM, above captive
DC, AC, Control & Communication Cables | 2.74 | 8.639% | [18 empty] | 5 | Delhi | Yes | CMD max of 4MW NM |  |  |  | Captive |  | on DC - CMD max of 4MWp NM, above captive
Earthing & LA, RMS and BOS | 1.6775 | 5.289% | [18 empty] | 6 | Gujarat | Yes |  |  | upto 1 MWp |  | BTM |  | on AC - 1 MW NM, above BTM
Rooftop Infra. (Walkways, cable tray, Ladder & Etc.) | 2.6452 | 8.34% | [18 empty] | 7 | Goa | Yes |  |  | 500KW NM |  | Net billing |  | on AC - 500KW NM,above captive
Ground Infra. (Fencing, road, soil test, land lavelling) | 0 | 0% | [18 empty] | 8 | Haryana | Yes |  |  | upto 500 kWp |  | Captive |  | on AC - 500KW NM,above captive
I&C and Civil works, Spare & Additional item's | -14.1475 | -44.6% | [18 empty] | 9 | Himachal Pradesh | Yes | till 50KWp NM, till 1MW NB |  |  |  | Captive |  | on DC - 50KWp NM, till 1MWp NB, above captive
Liaisoning, Net metering & AMC | 3.725 | 11.74% | [18 empty] | 10 | Jharkhand | Yes | upto 2 MWp DC |  |  |  | Captive |  | on DC - 2 MWp NM, above captive
Total per watt cost | 31.718 | 100% | [18 empty] | 11 | Karnataka | Yes | Eql. To CMD |  |  |  | Net billing |  | on DC - Eql. To CMD NM, above NB
[21 empty] | 12 | Kerala | Yes |  |  | CMD |  | Net metering compulsory |  | on AC - CMD NM, above captive
[21 empty] | 13 | Madhya Pradesh | Yes |  |  | upto 500 kWp |  | Captive |  | on AC - 500 KW NM, above captive
[21 empty] | 14 | Maharashtra | Yes |  |  | upto 1 MW AC |  | BTM |  | on AC - 1 MW NM, above BTM
[21 empty] | 15 | Odisha | >1 MWp | upto 500 kWp |  |  |  | Captive |  | on DC - 500 KWp NM, above captive
[21 empty] | 16 | Punjab | Yes |  |  | 500KW NM |  | Captive/Net billing |  | on AC - 500KW NM,above captive/NB
[21 empty] | 17 | Rajasthan | Yes | upto 1 MWp |  |  |  | Captive |  | on DC - 1 MWp NM, above captive
[21 empty] | 18 | Tamil Nadu | Yes |  |  | upto 1 MW AC |  | <1MW NB & >1MW captive |  | on AC - 1 MW NB, above captive
[21 empty] | 19 | Telangana | Yes | 500 KWp NM |  |  |  | BTM |  | on DC - 500 KWp NM, above BTM
[21 empty] | 20 | Uttar Pradesh | Yes | Netbilling on 2 MW |  |  |  | Captive |  | on DC - 2 MWp NM, above captive
[21 empty] | 21 | Uttarakhand | Yes | upto 1 MWp DC |  |  |  | Captive |  | on DC - 1 MWp NM, above captive
[21 empty] | 22 | West Bengal | >50 KWp |  |  | upto 500KWp |  | >500KWp Net billing |  | on AC - 500 KW NM, above NB
Back to top the of sheet
ESE Type LA with Counter
ESE Type LA with out Counter
4PEL Scope
Not Required
Client Scope
Already Exist
With Anchoring
With out Anchoring | [5 empty] | 345+6+32+20
Ballast
Sesonal tilt | [5 empty] | Cable tray | 345
Fixed tilt | [5 empty] | Base Clamp and Hardware | 38
Tracking | [5 empty] | Lord for Cable tray | 20
Existing plant capacity | 0 | KWp |  | Brick wall | 3000
|  |  |  | Prefab wall | 1850 |  | 928 | 2969.6 | Mtrs
Yes |  |  |  | Cabin type | 850 | Walkways | 430 | 399040
No | [5 empty] | Profile | 49 | 145510.4
Booster pump | 32125 |  |  |  |  | M-clamp and Hardware | 25 | 74240 |  | 50.9091
Not Required | 0 | [5 empty] | 8 | 23756.8 | [17 empty] | 1.1
PVC Water Tank 2000 Liters | 23000 |  |  |  |  | Lord for walkways | 2800 | 53.9927 | 55 profile for catrage
PVC Water Tank 5000 Liters | 51750 |  | PVC Water Tank 2000 Liters | 23000 |  |  |  | 642601.1927
Not Required | 0 |  | Not Required | 0
1 HP Motor | 3850
1.5HP Motor | 10500 | [5 empty] | Unit price | 3998.4
Not Required | [5 empty] | MMS Profile | 51 | 203918.4
| 0 |  | 0.3125 |  |  | End and mid clamp with Hardware | 29 | 115953.6 |  |  | CIF | 24.7
[6 empty] | Lord for MMS | 2800 | 339258.1818 |  |  | SGD | 1.145
[7 empty] | Total | 659130.1818 |  |  | Clearence | 1
|  |  | 1 HP Motor | 830 |  |  |  | 0.65913 |  |  |  | 29.2815
SMP5 | 79000 | for 1-2.999 MWp | 1.5HP Motor | 1850 |  | mms Profile calculation
SMP10 | 150000 | for 3-4.999MWp | Booster pump | 1850 |  | (No. of module Row +1)*2* (No. of module in coloum)
CMP11 | 200000 | for >=5Mwp | Not Required | 0
Lord calculation
per profile area is 120mm x 30mm for both sides
per profile area is 7200Sqmm
so, per profile consuming 12 mlts of lord clue
per catrage size is 400ml
|  |  | 1523 |  |  | per one catrage we can use to fix the profile is Apx. 33 nos | [17 empty] | 1K400734010
PLC Based | ABB/ Honeywell/ Equilent
Cloud Based | 4PEL Make
[11 empty] | $ | 74
|  | Need to update | [9 empty] | 21.6683
PLC Based | 3000000 | ABB/ Honeywell/ Equilent |  |  |  | Aluminium for sheds-W/O lord chemical | Unit price |  |  |  |  | 22
Cloud Based | 1000000 | 4PEL Make |  |  |  | Standing seam | 125
[6 empty] | Kliplock | 139
[6 empty] | SSB6 Profiles-120MM | 126
1CX4Sqmm DC Cable | [5 empty] | SSB2 Profiles-50MM | 83
Siechem | 58
Polycab | 0
Leoni | 0 |  |  |  |  | Aluminium for sheds-W lord chemical | Unit price
LAPP | 70 |  |  |  |  | Base 24 mm -ECO 70 | 59 | Booster pump
[6 empty] | Trapezoidal | 70
1CX6 Sqmm DC Cable | [5 empty] | Base 40 mm - SSP 1032 | 123 | [17 empty] | I&C (590 & 7200wp) |  | Capacities
Siechem | 78 |  |  |  |  | Land scape - 300MM | 179 | [19 empty] | 1-100 | 101-250 | 251-500 | 501-1000 | >1000
Polycab | 0 |  |  |  |  | Land scape - 250MM | 155 | [17 empty] | Plant Type | shed | 1550 | 1450 | 1400 | 1300 | 1250
Leoni | 0 | [5 empty] | 1 HP Motor | 80 | [17 empty] | Raised Shed | 1850 | 1757.5 | 1669.625 | 1586.1437 | 1506.8366
LAPP | 85 |  |  |  | 1.53 |  | 1.5HP Motor | 170 | [17 empty] | RCC | 3500 | 3250 | 3100 | 2900 | 2750
|  |  | 2 |  | 1.445 |  | Not Required | 170 | [17 empty] | RCC Raised | 6000 | 6000 | 5500 | 5500 | 5300
1350 | SMS Aluminium |  |  |  | 1.19 |  |  | 0 | [17 empty] | On Pillar | 6400 | 6200 | 6000 | 6000 | 6000
970 | HDG |  |  |  | 0.765 | 80 | 3CX2.5sqmm for motor wiring | [18 empty] | Ground | 2500 | 2450 | 2400 | 2300 | 2250
[5 empty] | 0.595 | 170 | 5CX2.5sqmm for motor wiring | [18 empty] | Parking | 6400 | 6000 | 5800 | 5600 | 5500
[5 empty] | 0.5525 | 170 | 5CX2.5sqmm for motor wiring | [18 empty] | Parking | 8000 | 7800 | 7500 | 7000 | 6700
[6 empty] | 0 | Not Required | [18 empty] | Floating | 2800 | 2660 | 2527 | 2400.65 | 2280.6175
Karam safety private limited | 1200
Lifegear safetech private limited | 1100 |  |  |  | Conventional type LA costing |  | 830 | Industrial wall socket box with MCB (Single phase two pole)
Omkar safety & power pvt ltd. | 1000 |  |  |  | Module watt peak | 540wp | 1850 | Industrial wall socket box with MCB (Three phase four pole)
[5 empty] | Capacity Ranges | per watt cost | 1850 | Industrial socket box with MCB (Three phase four pole)
[5 empty] | 100 | 76500 | 0 | Not Required
[5 empty] | 500 | 535185.1852
3 mtrs GI Earthing Electrode | 1400 |  |  |  | 1000 | 881481.4815
3 mtrs CU Earthing Electode | 4800 |  |  |  | 2500 | 956250
[5 empty] | 5000 | 1487500
[5 empty] | 10000 | 2762500
Pyranometer and Module Temp. sensor
Irradiation Sensor | 22000 | Surya logics |  |  |  | Walkways | Unit price
SMP 3 (Kipp& Zonen) & Module Temp sensor >1MW | 122000 | Kipp& Zonen |  |  |  | FRPL:1000xW:300xT:25 mm | 420
SMP 5 (Kipp& Zonen) & Module Temp sensor> 2.5MW | 272123 | Kipp& Zonen |  |  |  | FRPL:1000xW:600xT:25 mm | 900
SMP 10 (Kipp& Zonen) & Module Temp sensor > 5 MW | 524012 | Kipp& Zonen |  |  |  | GIL:1000xW:300xT:25 mm | 0
[6 empty] | GIL:1000xW:600xT:25 mm | 0
[6 empty] | HDGL:1000xW:300xT:25 mm | 0
[6 empty] | HDGL:1000xW:600xT:25 mm | 0
Optimizers (Solar Edge Inverter) model-S 1200 | 2500
Optimizers (Solar Edge Inverter) model-S 1500 | 3650 |  |  |  |  | Zero degree Walkways | Unit price
[6 empty] | FRPL:1000xW:300xT:25 mm | 420
Optimizers- Model-S 1200 | 2500 |  |  |  |  | FRPL:1000xW:600xT:25 mm | 900
Optimizers- Model-S 1400/ S 1500 | 3650 |  |  |  |  | GIL:1000xW:300xT:25 mm | 0
[6 empty] | GIL:1000xW:600xT:25 mm | 0
[6 empty] | HDGL:1000xW:300xT:25 mm | 0
[6 empty] | HDGL:1000xW:600xT:25 mm | 0
[6 empty] | Step Walkways | Unit price
[6 empty] | FRP | 462
[6 empty] | GI | 0
CEIG, NET Metering & Approvals Summary Sheet | [5 empty] | HDG | 0
State Name |  | Maharashtra
Capacity |  | DC | AC |  |  | DC cable tray | Unit price
Total Capcity (String Inverter LT) (DC & AC) |  | 400.52 | 300 |  |  | FRP50X50X2MM | 230.05
[6 empty] | FRP100X50X2MM | 339.19
[6 empty] | GI50X50X2MM | 282.48
[6 empty] | GI100X50X2MM | 365.94
[6 empty] | HDG50X50X2MM | 432.28
[6 empty] | HDG100X50X2MM | 603.48
HDG Cable Trays from ACJB to LT Panel for Shed (Ladder type) | per mtrs
4PEL Scope
Client Scope | 0
Using Existing Cable Tray | 0
100x75x2mm ladder type Cable Tray | GI | 332.64
100x75x2mm ladder type Cable Tray | HDG | 433.08
100x75x2mm ladder type Cable Tray | 0 | 440.64
Using Soil Trench | Soil Trench | 0
150x75x2mm ladder type Cable Tray | GI | 349.92
150x75x2mm ladder type Cable Tray | HDG | 456.84
150x75x2mm ladder type Cable Tray | 0 | 525.96
Using Soil Trench | Soil Trench | 0
200x75x2mm ladder type Cable Tray | GI | 368.28
200x75x2mm ladder type Cable Tray | HDG | 480.6 |  |  |  | 45455 | 545460
200x75x2mm ladder type Cable Tray | 0 | 612.36 |  |  |  | 45455 | 545460
Using Soil Trench | Soil Trench | 0
300X75X2mm Ladder Type Cable Tray | GI | 403.92
300X75X2mm Ladder Type Cable Tray | HDG | 525.96
300X75X2mm Ladder Type Cable Tray | 0 | 783
Using Soil Trench | Soil Trench | 0
400X75X2mm Ladder Type Cable Tray | GI | 439.56 |  |  |  | 1757
400X75X2mm Ladder Type Cable Tray | HDG | 572.4 |  |  |  | 2262
400X75X2mm Ladder Type Cable Tray | 0 | 954.72 |  |  |  | 2262
Using Soil Trench | Soil Trench | 0
500X75X2mm Ladder Type Cable Tray | GI | 475.2
500X75X2mm Ladder Type Cable Tray | HDG | 618.84
500X75X2mm Ladder Type Cable Tray | 0 | 1125.36
Using Soil Trench | Soil Trench | 0
600x75x2mm Ladder Type Cable Tray | GI | 510.84
600x75x2mm Ladder Type Cable Tray | HDG | 665.28
600x75x2mm Ladder Type Cable Tray | 0 | 1294.92
Using Soil Trench | Soil Trench | 0
FRP Cable Trays from Module to Inverter for Shed | Cost per mtrs | FRP Cable Trays from Module to Inverter for RCC | Cost per mtrs
50x50x2mm | 293 | 50x50x2mm | 266
100x50x2mm | 403 | 100x50x2mm | 383
150x50x2mm | 531 | 150x50x2mm | 503
200x50x2mm | 658 | 200x50x2mm | 588
300x50x2mm | 772 | 300x50x2mm | 702
GI Cable Trays Required (Internal wiring purpose) for Shed | Cost per mtrs | GI Cable Tray-RCC | Cost per mtrs
50x50x2mm | 347 | 50x50x2mm | 327
100x50x2mm | 497 | 100x50x2mm | 447
150x50x2mm | 617 | 150x50x2mm | 567
200x50x2mm | 751 | 200x50x2mm | 701
300x50x2mm | 980 | 300x50x2mm | 930
HDG Cable Trays Required (Internal wiring purpose) for shed | Cost per mtrs | HDG Cable Trays Required (Internal wiring purpose) for RCC | Cost per mtrs
50x50x2mm | 420 | 50x50x2mm | 400
100x50x2mm | 580 | 100x50x2mm | 534
150x50x2mm | 710 | 150x50x2mm | 671 |  | 473
200x50x2mm | 879 | 200x50x2mm | 809 |  | 671
300x50x2mm | 1154 | 300x50x2mm | 1084 |  | 924
Step Walkways Calculation for 300mm walways | FRP | GI | HDG |  | 220
Walkways 500 mm | 215 | 305 | 420
Supports | 230 | 300 | 300 |  |  | 50.9091
Walkways fixing clamps and Hardware | 60 | 60 | 60 |  | 12.7273
Walkways fixing Hardware | 44 | 44 | 44
Lord clue | 100 | 100 | 100
Per pices cost | 649 | 809 | 924
per mtr we need 2.2 Pieces | 1427.8 | 1779.8 | 2032.8 |  |  | Walkways 300 mm | 430
[6 empty] | Supports | 230
[6 empty] | Walkways fixing clamps & Hardware | 104
Zero degree Walkways Calculation for 300mm walways | FRP | GI | HDG |  |  | Lord clue
Walkways 300 mm | 430 | 610 | 840
Supports | 230 | 300 | 300
Walkways fixing clamps | 60 | 60 | 60
Walkways fixing Hardware | 44 | 44 | 44
Lord clue | 100 | 100 | 100
per mtr running cost | 864 | 1114 | 1344
100x75x2mm ladder type Cable Tray with 1.6mm Cover | 557
150x75x2mm ladder type Cable Tray with 1.6mm Cover | 632
500X75X2mm Ladder Type Cable Tray With 1.6mm Cover | 1006
200x75x2mm ladder type Cable Tray with 1.6mm Cover | 706
300X75X2mm Ladder Type Cable Tray with 1.6mm Cover | 854
500X75X2mm Ladder Type Cable Tray With 1.6mm Cover | 1006
400X75X2mm Ladder Type Cable Tray With 1.6mm Cover | 1003
500X75X2mm Ladder Type Cable Tray With 1.6mm Cover | 1150
500X75X2mm Ladder Type Cable Tray With 1.6mm Cover | 1006
600x75x2mm Ladder Type Cable Tray with 1.6mm cover | 1299
Using Soil Trench | 1050
500X75X2mm Ladder Type Cable Tray With 1.6mm Cover | 1006
100x75x2mm ladder type Cable Tray with 1.6mm Cover | 456
500X75X2mm Ladder Type Cable Tray With 1.6mm Cover | 1006
150x75x2mm ladder type Cable Tray with 1.6mm Cover | 525
200x75x2mm ladder type Cable Tray with 1.6mm Cover | 593
500X75X2mm Ladder Type Cable Tray With 1.6mm Cover | 1006
300X75X2mm Ladder Type Cable Tray with 1.6mm Cover | 731
400X75X2mm Ladder Type Cable Tray With 1.6mm Cover | 868
500X75X2mm Ladder Type Cable Tray With 1.6mm Cover | 1006
600x75x2mm Ladder Type Cable Tray with 1.6mm cover | 1143
Using Soil Trench | 1050
Name of the state |  | Return value of NM limit
Andhra Pradesh |  | on DC - 500 KWp NM, till 1MWp NB, above BTM |  |  | BTM
Assam |  | on DC - 500 KWp NM, above BTM |  |  | BTM
Bihar |  | on DC - 1 MWp NM, above captive |  |  | Captive
Chhattisgarh |  | on AC - 500 KW NM, above captive |  |  | Captive
Delhi |  | on DC - CMD max of 4MWp NM, above captive |  |  | Captive
Gujarat |  | on AC - 1 MW NM, above BTM |  |  | BTM
Goa |  | on AC - 500KW NM,above captive |  |  | Captive
Haryana |  | on AC - 500KW NM,above captive |  |  | Captive
Himachal Pradesh |  | on DC - 50KWp NM, till 1MWp NB, above captive |  |  | Captive
Jharkhand |  | on DC - 2 MWp NM, above captive |  |  | Captive
Karnataka |  | on DC - Eql. To CMD NM, above NB |  |  | Net billing
Kerala |  | on AC - CMD NM, above captive |  |  | Net metering compulsory
Madhya Pradesh |  | on AC - 500 KW NM, above captive |  |  | Captive
Maharashtra |  | on AC - 1 MW NM, above BTM |  |  | BTM
Odisha |  | on DC - 500 KWp NM, above captive |  |  | Captive
Punjab |  | on AC - 500KW NM,above captive/NB |  |  | Captive/Net billing
Rajasthan |  | on DC - 1 MWp NM, above captive |  |  | Captive
Tamil Nadu |  | on AC - 1 MW NB, above captive |  |  | <1MW NB & >1MW captive
Telangana |  | on DC - 500 KWp NM, above BTM |  |  | BTM
Uttar Pradesh |  | on DC - 2 MWp NM, above captive |  |  | Captive
Uttarakhand |  | on DC - 1 MWp NM, above captive |  |  | Captive
West Bengal |  | on AC - 500 KW NM, above NB |  |  | >500KWp Net billing
Note on A31: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: It will convert sunlight into electricity
Note on A34: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: It will convert the direct current (DC) electricity generated by solar panels into alternating current (AC) electricity
Note on A35: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: It will convert the direct current (DC) electricity generated by solar panels into alternating current (AC) electricity
Note on A36: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: It will convert the direct current (DC) electricity generated by solar panels into alternating current (AC) electricity
Note on A37: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: It will convert the direct current (DC) electricity generated by solar panels into alternating current (AC) electricity
Note on A38: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: It will convert the direct current (DC) electricity generated by solar panels into alternating current (AC) electricity
Note on A39: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: It will convert the direct current (DC) electricity generated by solar panels into alternating current (AC) electricity
Note on A40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: It will convert the direct current (DC) electricity generated by solar panels into alternating current (AC) electricity
Note on A41: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: It will convert the direct current (DC) electricity generated by solar panels into alternating current (AC) electricity
Note on A42: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: It will convert the direct current (DC) electricity generated by solar panels into alternating current (AC) electricity
Note on A43: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: It will convert the direct current (DC) electricity generated by solar panels into alternating current (AC) electricity
Note on A44: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Warranty extended to 10 years
Note on A47: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: MMS is securely supporting and positioning solar panels, ensuring they capture the maximum amount of sunlight for optimal energy generation
Note on A48: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: MMS is securely supporting and positioning solar panels, ensuring they capture the maximum amount of sunlight for optimal energy generation
Note on A49: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: End clamps secure the ends of the solar panel array to the mounting rails, preventing them from sliding or shifting. Mid clamps, on the other hand, are used to secure adjacent panels to each other along the mounting rails, maintaining proper spacing and stability.
Note on A50: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: MMS is securely supporting and positioning solar panels, ensuring they capture the maximum amount of sunlight for optimal energy generation
Note on A51: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: RCC mounted solar structures, also known as RCC roof mounts, are mounting systems that use reinforced cement concrete to securely support solar panels on rooftops. They are a popular choice for installations on buildings with flat RCC roofs, especially in commercial and industrial settings
Note on A52: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: RCC raised mounted solar structures are a type of elevated solar panel installation, where the solar panels are mounted on a Reinforced Cement Concrete structure built above a flat RCC roof.
Note on A53: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: RCC raised mounted solar structures are a type of elevated solar panel installation, where the solar panels are mounted on a Reinforced Cement Concrete structure built above a flat RCC roof.
Note on A54: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Ground-mounted solar structures are frameworks that hold solar panels securely on the ground, in contrast to rooftop or carport installations. These structures are crucial for ground-based solar installations, ensuring stability and optimal positioning for maximizing sunlight exposure. They are a popular choice for both residential and commercial projects, especially for those with large plots of land or challenging roof spaces
Note on A55: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Solar car parking structures, also known as solar carports, are innovative solutions that integrate solar panels into the design of car parking facilities, providing shade and generating clean electricity. These structures offer a wide array of benefits, both environmental and financial
Note on A56: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Solar car parking structures, also known as solar carports, are innovative solutions that integrate solar panels into the design of car parking facilities, providing shade and generating clean electricity. These structures offer a wide array of benefits, both environmental and financial
Note on A57: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Floating mounted solar structures, also known as floating photovoltaic (FPV) systems or floatovoltaics, represent an innovative approach to solar energy generation, deploying solar panels on the surface of water bodies such as lakes, reservoirs, and industrial ponds. This technology offers a compelling solution, especially in areas where land availability is scarce or expensive, combining energy production with water management benefits.
Note on A58: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Beyond the solar panels themselves, a crucial element of any solar power system is the hardware that secures and supports the panels. This "hardware," often referred to as the Module Mounting Structure (MMS) or racking system, comprises various components designed to ensure the stability, longevity, and optimal performance of the solar array.
Note on A61: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: In solar photovoltaic (PV) systems, the Direct Current Distribution Box (DCDB) plays a crucial role in safely managing and distributing the DC power generated by the solar panels to the inverter. A key aspect of a well-designed DCDB is the inclusion of essential safety components like fuses and a Surge Protection Device (SPD). These elements work in tandem to protect the system from potential damage and ensure safe operation
Note on A62: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: An ACDB with Breaker & SPD is an Alternating Current Distribution Box, a safety enclosure for solar or grid power, containing Miniature Circuit Breakers (MCBs) to protect against overloads and Surge Protection Devices (SPDs) to divert excess voltage from lightning or grid issues, ensuring safe power flow from the inverter to your home's electrical system
Note on A63: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Optimizers utilize Maximum Power Point Tracking (MPPT) technology at the individual panel level. This means they constantly monitor the voltage and current of each panel, adjusting its electrical characteristics to ensure it operates at its peak power output, regardless of the performance of other panels in the array.
Note on A64: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: DC (Direct Current) fuses are specialized safety devices designed to protect solar photovoltaic (PV) systems, and other DC electrical circuits from damage caused by over currents and short circuits. These fuses are crucial for ensuring the safety and longevity of solar installations.
Note on A65: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Used for convert the cu. Cable into Al cable without a breaker
Note on A68: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: "spare feeder extension" within an AC Distribution Box (ACDB) refers to the provision of extra space, terminals, and potentially even pre-installed but unutilized circuit breakers or switches within the ACDB, allowing for the future expansion or modification of the AC power distribution system.
Note on A69: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To combine the multiple inverters input into single out ( all the input & out having dedicated breakers)
Note on A70: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: An UVR is a safety device designed to trip a circuit breaker automatically when the voltage in the circuit drops below a predetermined safe level. This is critical for protecting equipment from damage that can occur due to low voltage conditions.
Note on A71: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: A contactor panel is an electrical control box housing heavy-duty, electrically operated switches (contactors) that safely control solar ACCB Panel
Note on A72: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: An isolation panel essentially houses one or more isolator switches, which are manually operated mechanical switches designed to create a visible break in an electrical circuit, ensuring that no power passes through it. This physical separation is vital for protecting individuals and equipment during work on the system.
Note on A75: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Transmit direct current (DC) electricity within a solar power system, specifically connecting solar panels to Inverters
Note on A76: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Transmit direct current (DC) electricity within a solar power system, specifically connecting solar panels to Inverters
Note on A79: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Cable used for inverter to ACJB box. We can’t use AL cable to the small inverters so we are using cu. Cable for short distance then it will convert into AL cable.
Note on A80: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Cable used for inverter to ACJB box. We can’t use AL cable to the small inverters so we are using cu. Cable for short distance then it will convert into AL cable.
Note on A83: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Cable used from Inverter to ACCB Panel it having insulation material is XLPE
Note on A84: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Cable used from Inverter to ACCB Panel it having insulation material is XLPE
Note on A85: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Cable used from Inverter to ACCB Panel it having insulation material is XLPE
Note on A86: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Cable used from Inverter to ACCB Panel it having insulation material is XLPE
Note on A87: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Cable used from Inverter to ACCB Panel it having insulation material is XLPE
Note on A88: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Cable used from Inverter to ACCB Panel it having insulation material is XLPE
Note on A89: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Cable used from Inverter to ACCB Panel it having insulation material is XLPE
Note on A90: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Cable used from Inverter to ACCB Panel it having insulation material is XLPE
Note on A91: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Cable used from Inverter to ACCB Panel it having insulation material is XLPE
Note on A92: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Cable used from Inverter to ACCB Panel it having insulation material is XLPE
Note on A93: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Cable used from Inverter to ACCB Panel it having insulation material is XLPE
Note on A96: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Cable used for Solar ACCB Panel to Client termination cable having XLPE protection.
Note on A97: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Cable used for Solar ACCB Panel to Client termination cable having XLPE protection.
Note on A98: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Cable used for Solar ACCB Panel to Client termination cable having XLPE protection.
Note on A99: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Cable used for Solar ACCB Panel to Client termination cable having XLPE protection.
Note on A100: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Cable used for Solar ACCB Panel to Client termination cable having XLPE protection.
Note on A101: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Cable used for Solar ACCB Panel to Client termination cable having XLPE protection.
Note on A102: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Cable used for Solar ACCB Panel to Client termination cable having XLPE protection.
Note on A103: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Cable used for Solar ACCB Panel to Client termination cable having XLPE protection.
Note on A104: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Cable used for Solar ACCB Panel to Client termination cable having XLPE protection.
Note on A105: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Cable used for Solar ACCB Panel to Client termination cable having XLPE protection.
Note on A106: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Cable used for Solar ACCB Panel to Client termination cable having XLPE protection.
Note on A109: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Module frame earthing, also known as array earthing or grounding, is a critical safety and performance measure in solar PV systems. It involves securely connecting the metallic frames of the solar panels and their mounting structures to the overall earthing system of the solar installation.
Note on A110: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Ensuring the inverter is properly earthed or grounded is paramount for safety and system protection. The inverter earthing cable is the dedicated conductor that connects the metallic chassis of the inverter to the main earthing system of the installation.
Note on A111: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Ensuring the inverter is properly earthed or grounded is paramount for safety and system protection. The inverter earthing cable is the dedicated conductor that connects the metallic chassis of the inverter to the main earthing system of the installation.
Note on A112: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Ensuring the inverter is properly earthed or grounded is paramount for safety and system protection. The inverter earthing cable is the dedicated conductor that connects the metallic chassis of the inverter to the main earthing system of the installation.
Note on A113: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Ensuring the inverter is properly earthed or grounded is paramount for safety and system protection. The inverter earthing cable is the dedicated conductor that connects the metallic chassis of the inverter to the main earthing system of the installation.
Note on A114: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Ensuring the inverter is properly earthed or grounded is paramount for safety and system protection. The inverter earthing cable is the dedicated conductor that connects the metallic chassis of the inverter to the main earthing system of the installation.
Note on A115: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Cable used for DGPD & ZFD control and power supply.
Note on A116: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Used for power supply to the water pump single phase supply
Note on A117: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Used for power supply to the water pump for three phase supply
Note on A118: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Used for take a communication signal from inverter to RMS device
Note on A119: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Used for take a communication signal from inverter to RMS device
Note on A120: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Used for Periphery lighting system power supply cable.
Note on A123: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Early Streamer Emission (ESE) lightning arresters represent an advanced form of lightning protection system that aims to proactively intercept lightning strikes before they can reach a protected structure & This ionization process creates a path of highly conductive, ionized air, which functions as an "early streamer" that extends upward from the ESE arrester towards the downward leader of an approaching lightning strike.
Note on A124: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: In the context of lightning protection, an "Air Terminal," also commonly known as a lightning rod, is the initial point of contact for a lightning strike within an external lightning protection system. It is designed to intercept lightning strikes before they can directly hit and potentially damage a structure, such as a building or a solar installation.
Note on A125: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Utilizing a 3-meter GI (Galvanized Iron) chemical earthing electrode is a common and effective practice for grounding solar panel installations, particularly rooftop systems & ground mounted
Note on A126: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: It's designed to protect the earthing connection, facilitate maintenance and testing, and ensure the overall safety and integrity of the electrical installation
Note on A127: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Bentonite powder, commonly packaged in 25 kg bags, is a highly effective and widely used backfill material in earthing or grounding systems, especially in areas with high soil resistivity. Its unique properties make it an ideal choice for enhancing the conductivity of the surrounding soil, ensuring a low-resistance path for fault currents and voltage surges to safely dissipate into the ground
Note on A128: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: GI (Galvanized Iron) earthing strips are flat conductors used in earthing or grounding systems. They are made from steel strips that have been hot-dip galvanized, meaning they are coated with a layer of zinc. This zinc coating provides corrosion resistance, making the strips more durable and suitable for use in various environments, including outdoor installations and burial underground
Note on A129: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: GI (Galvanized Iron) earthing strips are flat conductors used in earthing or grounding systems. They are made from steel strips that have been hot-dip galvanized, meaning they are coated with a layer of zinc. This zinc coating provides corrosion resistance, making the strips more durable and suitable for use in various environments, including outdoor installations and burial underground
Note on A130: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: GI (Galvanized Iron) earthing strips are flat conductors used in earthing or grounding systems. They are made from steel strips that have been hot-dip galvanized, meaning they are coated with a layer of zinc. This zinc coating provides corrosion resistance, making the strips more durable and suitable for use in various environments, including outdoor installations and burial underground
Note on A131: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: GI (Galvanized Iron) earthing strips are flat conductors used in earthing or grounding systems. They are made from steel strips that have been hot-dip galvanized, meaning they are coated with a layer of zinc. This zinc coating provides corrosion resistance, making the strips more durable and suitable for use in various environments, including outdoor installations and burial underground
Note on A134: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Walkways in solar power plants enhance safety by providing stable paths for workers, reducing accident risks
Note on A135: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Safety: Step walkways, especially with an inclination and non-slip surfaces, minimize the risk of slips, trips, and falls for workers accessing solar panels on sloped roofs
Note on A136: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: A 0-degree walkway provides a level surface for technicians to safely walk across a solar installation, reducing the risk of slips, trips, and falls associated with uneven terrain or sloped surfaces.
Note on A139: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: DC cable trays are structural elements used to support, organize, and protect the DC (direct current) cables that connect solar panels to inverters
Note on A143: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: AC cable trays are a vital part of managing the alternating current (AC) wiring generated by inverters in a solar power system. AC cable trays facilitate the safe and organized routing of these AC cables, offering numerous benefits
Note on A144: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: AC cable trays are a vital part of managing the alternating current (AC) wiring generated by inverters in a solar power system. AC cable trays facilitate the safe and organized routing of these AC cables, offering numerous benefits
Note on A145: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: AC cable trays are a vital part of managing the alternating current (AC) wiring generated by inverters in a solar power system. AC cable trays facilitate the safe and organized routing of these AC cables, offering numerous benefits
Note on A146: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: AC cable trays are a vital part of managing the alternating current (AC) wiring generated by inverters in a solar power system. AC cable trays facilitate the safe and organized routing of these AC cables, offering numerous benefits
Note on A147: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: AC cable trays are a vital part of managing the alternating current (AC) wiring generated by inverters in a solar power system. AC cable trays facilitate the safe and organized routing of these AC cables, offering numerous benefits
Note on A148: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: AC cable trays are a vital part of managing the alternating current (AC) wiring generated by inverters in a solar power system. AC cable trays facilitate the safe and organized routing of these AC cables, offering numerous benefits
Note on A149: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: AC cable trays are a vital part of managing the alternating current (AC) wiring generated by inverters in a solar power system. AC cable trays facilitate the safe and organized routing of these AC cables, offering numerous benefits
Note on A152: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: AC cable trays are a vital part of managing the alternating current (AC) wiring generated by inverters in a solar power system. AC cable trays facilitate the safe and organized routing of these AC cables, offering numerous benefits
Note on A153: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: AC cable trays are a vital part of managing the alternating current (AC) wiring generated by inverters in a solar power system. AC cable trays facilitate the safe and organized routing of these AC cables, offering numerous benefits
Note on A154: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: AC cable trays are a vital part of managing the alternating current (AC) wiring generated by inverters in a solar power system. AC cable trays facilitate the safe and organized routing of these AC cables, offering numerous benefits
Note on A155: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: AC cable trays are a vital part of managing the alternating current (AC) wiring generated by inverters in a solar power system. AC cable trays facilitate the safe and organized routing of these AC cables, offering numerous benefits
Note on A156: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: AC cable trays are a vital part of managing the alternating current (AC) wiring generated by inverters in a solar power system. AC cable trays facilitate the safe and organized routing of these AC cables, offering numerous benefits
Note on A157: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: AC cable trays are a vital part of managing the alternating current (AC) wiring generated by inverters in a solar power system. AC cable trays facilitate the safe and organized routing of these AC cables, offering numerous benefits
Note on A158: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: AC cable trays are a vital part of managing the alternating current (AC) wiring generated by inverters in a solar power system. AC cable trays facilitate the safe and organized routing of these AC cables, offering numerous benefits
Note on A161: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: "Monkey ladder" is a term commonly used to refer to a type of ladder designed for accessing challenging or elevated areas, and it finds the solar power plants
Note on A162: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Staircase-step ladders, specifically designed for rooftop access in solar installations and other industries, are a form of fixed ladder with treads or steps rather than rungs, providing a more comfortable and secure climbing experience compared to traditional vertical ladders. They are an essential part of a comprehensive safety system for rooftop work, particularly for accessing PV panels for maintenance and inspection.
Note on A163: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Typically used for raised structures to cleaning the modules
Note on A164: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: n architectural and industrial contexts, a roof monitor is a raised structure that runs along the ridge of a double-pitched roof, featuring its own roof parallel to the main one. Will arrange the crossover plate form to the structure.
Note on A165: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: We will access the lower plant to upper plant by using ladder
Note on A166: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Rooftop solar panel installations necessitate robust safety measures, and roof edge railings are paramount among them. The presence of numerous panels on the roof often reduces walking space and increases the likelihood of accidental falls, highlighting the crucial need for adequate fall protection
Note on A167: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Skylight mesh protection systems are crucial safety barriers designed to prevent falls through skylights and roof openings. These systems, typically constructed from robust materials like galvanized steel or aluminum, are engineered to withstand significant weight and impact, ensuring a secure environment for individuals working or moving on rooftops.
Note on A168: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Skylight mesh protection systems are crucial safety barriers designed to prevent falls through skylights and roof openings. These systems, typically constructed from robust materials like galvanized steel or aluminum, are engineered to withstand significant weight and impact, ensuring a secure environment for individuals working or moving on rooftops.
Note on A169: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Skylight mesh protection systems are crucial safety barriers designed to prevent falls through skylights and roof openings. These systems, typically constructed from robust materials like galvanized steel or aluminum, are engineered to withstand significant weight and impact, ensuring a secure environment for individuals working or moving on rooftops.
Note on A170: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Skylight mesh protection systems are crucial safety barriers designed to prevent falls through skylights and roof openings. These systems, typically constructed from robust materials like galvanized steel or aluminum, are engineered to withstand significant weight and impact, ensuring a secure environment for individuals working or moving on rooftops.
Note on A171: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Turbo vent cover mesh protection systems are crucial safety barriers designed to prevent falls through skylights and roof openings. These systems, typically constructed from robust materials like galvanized steel or aluminum, are engineered to withstand significant weight and impact, ensuring a secure environment for individuals working or moving on rooftops.
Note on A172: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Lifelines, also known as horizontal lifeline systems or safety line systems, are crucial components of fall protection for workers installing, maintaining, or inspecting solar panels on rooftops. These systems are particularly important given the inherent fall hazards associated with working on rooftops, often at considerable heights, and the presence of numerous solar panels that can limit movement and access.
Note on A173: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: These posts act as strong, strategically placed anchor points to which the lifeline cable is attached, allowing workers to move freely and safely across the rooftop during installation, maintenance, or inspections
Note on A174: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: It's a device that connects a worker's safety harness to the lifeline (a cable or rope), allowing them to move freely along the line while remaining continuously connected and protected against falls
Note on A175: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: A vertical lifeline system is a crucial fall protection solution designed for workers who need to ascend or descend ladders, stairways, or other vertical structures at height.
Note on A176: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Gutters help direct rainwater runoff from the roof and the solar panels away from the building's foundation, preventing potential damage to walls, foundations, and landscaping.
Note on A177: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Downspout drop outlet, is the component that connects a rain gutter to a downspout, directing rainwater runoff from the roof and, by extension, the solar panels, into the drainage system.
Note on A180: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: A remote monitoring system in the context of solar energy is a technology-driven solution that allows users to track, measure, and analyze the performance of their solar power system from a remote location, without needing to be physically present at the site. These systems, often based on the Internet of Things (IoT), are a blend of hardware and software designed to provide real-time insights and facilitate proactive management of solar installations
Note on A181: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: A cloud-based SCADA (Supervisory Control and Data Acquisition) system combines the functionalities of traditional SCADA systems with the scalability, flexibility, and accessibility offered by cloud computing platforms
Note on A182: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Irradiance sensors are essential for monitoring the actual power generation of solar panels and identifying issues impacting efficiency.
Note on A183: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: A pyranometer is an instrument used to measure solar irradiance, or the power of sunlight hey are essential for designing, optimizing, and monitoring solar power systems, including photovoltaic (PV) plants, by assessing the available solar resource and panel performance (lobal horizontal irradiance (GHI) )
Note on A184: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: A pyranometer is an instrument used to measure solar irradiance, or the power of sunlight hey are essential for designing, optimizing, and monitoring solar power systems, including photovoltaic (PV) plants, by assessing the available solar resource and panel performance (lobal horizontal irradiance (GHI) )
Note on A185: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: A thermistor-based solar module temperature sensor is specifically designed to measure the surface or cell temperature of photovoltaic (PV) modules, playing a crucial role in optimizing their performance and extending their lifespan
Note on A186: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: An ambient temperature sensor for solar installations measures the temperature of the air surrounding the solar panels, distinct from the temperature of the panel surface itself. This data is crucial for understanding the overall environmental conditions influencing the solar system's performance.
Note on A187: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: An anemometer is an instrument used to measure wind speed and, sometimes, wind direction. While often associated with wind energy, anemometers are also vital in solar power installations, contributing significantly to both system performance and safety.
Note on A188: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: A rain gauge sensor is an instrument specifically designed to measure and record the amount of liquid precipitation (rainfall) over a set period.
Note on A189: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: A weather station tripod mounting stand is a structure specifically designed to securely install and position the various sensors of a weather station for accurate and reliable data collection. These stands are crucial in applications where precise weather data is required, such as in solar power plants and environmental monitoring.
Note on A190: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: A solar data logger, also known as a data recorder or data acquisition system, is an electronic device that automatically collects, records, and stores data from various sensors and components within a solar PV (photovoltaic) power system. This stored data can then be analyzed to monitor and optimize the performance of the solar installation.
Note on A191: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: A humidity sensor, often bundled with an ambient temperature sensor and sometimes housed in a radiation shield, plays a vital role in solar PV (photovoltaic) power plants by providing data about the amount of moisture in the surrounding atmosphere
Note on A192: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: A zero feeding device, more commonly known as a Zero Export Device (ZED) or Zero Export Controller, is a smart energy management tool used in grid-tied solar photovoltaic (PV) systems to prevent the export of excess solar power back into the utility grid. Its primary function is to ensure that all solar energy generated is either consumed by local loads within the premises. thereby preventing any surplus energy from being fed into the grid.
Note on A193: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: A DG protection device, in the context of solar energy, specifically refers to a control and protection system designed to safeguard a Diesel Generator (DG) that operates in conjunction with a solar PV (photovoltaic) system. These devices, often called DG-PV synchronizers or zero export devices when combined with the zero export function, are essential for ensuring the safe, efficient, and reliable integration of solar power with existing diesel generator backup systems.
Note on A196: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The robust precast wall and fencing system protects solar panels, inverters, cabling, and other sensitive equipment from physical damage due to intrusion or vandalism.
Note on A197: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The main gate is a critical component of the solar plant's perimeter security system, deterring unauthorized access and protecting valuable assets like solar panels, inverters, cables, and other electrical equipment from theft and vandalism.
Note on A198: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: olar power plants contain valuable equipment (solar panels, inverters, cabling), making them attractive targets for theft and vandalism. Well-placed and adequately bright street lights deter intruders and facilitate surveillance, especially in remote locations or during nighttime hours
Note on A199: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Solar power plants contain valuable equipment (solar panels, inverters, cabling), making them attractive targets for theft and vandalism. Well-placed and adequately bright street lights deter intruders and facilitate surveillance, especially in remote locations or during nighttime hours
Note on A203: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Lord Chemical, now a part of Parker Hannifin, offers high-performance adhesive solutions specifically designed for solar rooftop installations. Their focus is on providing non-penetrating solutions, meaning these adhesives allow for the mounting of solar panels without drilling or bolting onto the roof, thereby eliminating potential leakage points and preserving the roof's integrity and warranty
Note on A204: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Lord Chemical, now a part of Parker Hannifin, offers high-performance adhesive solutions specifically designed for solar rooftop installations. Their focus is on providing non-penetrating solutions, meaning these adhesives allow for the mounting of solar panels without drilling or bolting onto the roof, thereby eliminating potential leakage points and preserving the roof's integrity and warranty
Note on A205: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To fixing the earth strip in the wall or any other fixing location
Note on A206: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Used for fixing the earth strip into the wall.
Note on A207: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Hardware use for fixing the earthstrip joint and DC cable tray fixing
Note on A208: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: It will holding the DC cable tray from the ground level
Note on A211: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To Fix the walkways.
Note on A212: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The "SSP 1045 Profile 75mm" refers to a specific type of section or rail used within the Walkways support of a solar power plant
Note on A213: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The "SSP 5 Profile 50mm" refers to a specific type of section or rail used within the Walkways support of a solar power plant
Note on A214: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Walkway jointers, also referred to as walkway connectors or joining plates, are crucial components used to securely link individual walkway sections together, creating a continuous and stable pathway across the installation
Note on A215: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: By providing designated pathways, walkways prevent foot traffic directly on the solar panels and the roof surface, minimizing potential damage and reducing wear and tear on the roofing system itself.
Note on A216: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: By providing robust mechanical support, clamps ensure the stability of the cable tray system, even when loaded with numerous cables or exposed to environmental factors like wind.
Note on A217: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The flexible pipes shield the cables from physical damage, including potential impacts, crushing, and wear and tear. Flexible conduit protects against UV rays, water, temperature changes, rodents, vermin, vandalism, and cable theft.
Note on A219: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: An industrial wall socket box with an integrated Single-phase, Two-pole MCB (Miniature Circuit Breaker) is a vital component for ensuring safe and reliable power distribution in booster pump systems
Note on A220: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: An industrial wall socket box with an integrated Three-phase, Four-pole MCB (Miniature Circuit Breaker) is a vital component for ensuring safe and reliable power distribution in booster pump systems
Note on A221: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Module water drainage clips, also known as solar panel drain clips or water guide clamps, are small, yet highly effective accessories designed to improve the performance and lifespan of solar panels by facilitating efficient water drainage from the module's surface and frame.
Note on A222: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Module water drainage clips, also known as solar panel drain clips or water guide clamps, are small, yet highly effective accessories designed to improve the performance and lifespan of solar panels by facilitating efficient water drainage from the module's surface and frame.
Note on A223: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Nylon cable ties, particularly in the 150mm length, are a widely used solution for bundling and securing cables in solar power installations
Note on A224: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Nylon cable ties, particularly in the 200mm length, are a widely used solution for bundling and securing cables in solar power installations
Note on A225: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Nylon cable ties, particularly in the 300mm length, are a widely used solution for bundling and securing cables in solar power installations
Note on A226: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Nylon cable ties, particularly in the 450mm length, are a widely used solution for bundling and securing cables in solar power installations
Note on A227: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Stainless steel (SS) cable ties, particularly in the 200mm length, are a suitable solution for securing and organizing electrical cables in solar power installations option for outdoor application
Note on A228: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Stainless steel (SS) cable ties, particularly in the 300mm length, are a suitable solution for securing and organizing electrical cables in solar power installations option for outdoor application
Note on A229: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Stainless steel (SS) cable ties, particularly in the 500mm length, are a suitable solution for securing and organizing electrical cables in solar power installations option for outdoor application
Note on A230: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 3-meter galvanized iron (GI) pipe used as a mounting support for the Lightning Arrester, providing required height for effective lightning protection and ensuring corrosion-resistant durability.
Note on A231: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Galvanized iron (GI) wire used to support the Lightning Arrester (LA) structure, ensuring stability and proper earthing connection. Provides mechanical strength and corrosion resistance for long-term safety.
Note on A232: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: MC4 connectors are the industry standard for connecting solar panels in photovoltaic (PV) systems. They are specifically designed for outdoor DC applications, providing a secure, weatherproof, and durable connection between solar panels and other components like inverters or charge controllers.
Note on A233: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: In-line DC fuse holders with male and female connectors are essential safety devices used in solar photovoltaic (PV) installations, particularly for protecting individual strings of solar panels or DC circuits from overcurrent conditions. These components provide a compact, reliable, and easily accessible method for integrating fuse protection directly into the wiring of a solar system
Note on A234: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Clamps secure DC cables, preventing them from hanging loosely or rubbing against sharp edges, which can lead to abrasion, damage, or even short circuits. They also protect cables from potential damage from wind, snow, animals (e.g., rodents), and other environmental factors
Note on A235: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: CO₂ fire extinguisher is used for electrical and flammable liquid fires. Displaces oxygen to extinguish fire without damaging electrical equipment; mandatory in control rooms and HT panel areas
Note on A236: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Multipurpose fire extinguisher (Class A, B, C) suitable for solid, liquid, and electrical fires. Essential for quick response to diverse fire types and mandatory for safety compliance in solar plants
Note on A237: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To provide immediate fire-fighting capability for small fires. Fire buckets (filled with sand/water) with stand and canopy are placed in accessible locations to meet safety compliance and control fire emergencies quickly.
Note on A238: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Solvent cement chemically fuses the surfaces of PVC/CPVC pipes and fittings, creating a solid, permanent bond that effectively prevents leaks and protects electrical wiring from moisture and dust, crucial for outdoor solar applications.
Note on A239: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: They shield the conduit interiors from dust, dirt, and other debris that can accumulate and potentially affect cable insulation or performance.
Note on A240: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The primary purpose of heat shrink sleeves is to provide electrical insulation around wires, cables, and connectors, preventing short circuits and electrical hazards. This is crucial for power cables, which carry higher currents and voltages.
Note on A241: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The primary purpose of heat shrink sleeves is to provide electrical insulation around wires, cables, and connectors, preventing short circuits and electrical hazards. This is crucial for power cables, which carry higher currents and voltages.
Note on A242: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The primary function is to provide electrical insulation for wire joints, splices, and other connections, preventing electrical leakage, short circuits, and potential hazards like electric shock or fire.
Note on A243: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Cable Marking Ferrules: As mentioned in a previous response, ferrules are used to identify cables, often with pre-printed or custom-printed legends (numbers, letters, or symbols).
Note on A244: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Copper ring lugs are indispensable components for ensuring the safe and reliable earthing of solar panel module frames. In a solar installation, proper grounding of the module frames is critical to prevent electric shock hazards and protect the entire system from potential damage due to lightning strikes or electrical faults
Note on A245: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Hardware used for walkways fixing
Note on A246: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Used for module cleaning tap to the module nearest area
Note on A247: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Used for internal water piping system for solar plant area.
Note on A248: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To connect the water pipe system where T junction is needed
Note on A249: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To connect the water pipe system where L junction is needed
Note on A250: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To connect the water pipe system where water outlet is needed
Note on A251: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Used to connect the straight pipe line continuations.
Note on A252: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To fix the junction, L, T and coupler connection.
Note on A253: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To fix the water pipeline in mechanically.
Note on A254: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: It is used on end water connection.
Note on A255: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: An MTA features external, outward-facing threads. It is designed to be inserted into a component with internal, inward-facing threads to create a secure connection.
Note on A256: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Making it easier to remove components like valves or filters for servicing.
Note on A257: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Used to give the continues supply to the Wattmon even when power supply disconnected till one hour
Note on A258: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To protect the Wattmon and sensors from the surge
Note on A259: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: An earth pit nameplate, or identification plate, is a crucial component for any earthing or grounding system, providing vital information for inspection, maintenance, and safety. It serves as a permanent label on or near the earth pit cover, enabling clear identification and tracking of the earthing system, thereby enhancing the overall safety and reliability of the electrical installation
Note on A260: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Sign boards and charts highlight specific risks associated with solar power systems, including electrical hazards (high voltage, shock risk), fall hazards (working at heights), fire hazards, and chemical hazards
Note on A261: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Company name bord fixed on main area
Note on A262: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To indicate the underground route of LT cables for easy identification and to prevent accidental damage during excavation. Used along cable paths at regular intervals for safety and maintenance reference.
Note on A263: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To protect personnel from electric shock while working near LT equipment. ISI-marked insulating mat as per IS 15652 is mandatory in LT panel/switchgear areas for safety compliance
Note on A264: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Used for Underground cable transmission through road crossing area
Note on A265: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Double-Wall Corrugated (DWC) pipes, typically used for DC cabling for ground mounted plant.
Note on A266: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Double-Wall Corrugated (DWC) pipes, typically used for DC cabling for ground mounted plant. Where ever T junction are needed.
Note on A267: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Double-Wall Corrugated (DWC) pipes, typically used for DC cabling for ground mounted plant. Where ever L Bends are needed.
Note on A268: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Double-Wall Corrugated (DWC) pipes, typically used for DC cabling for ground mounted plant. Where ever pipe extension is needed
Note on A269: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Used to store the water for module cleaning
Note on A270: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Used to store the water for module cleaning
Note on A271: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To pump the water from ground level to rooftop or solar plant area with sufficient water pressure to clean the solar modules.
Note on A272: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To pump the water from ground level to rooftop or solar plant area with sufficient water pressure to clean the solar modules.
Note on A273: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To pump the water from ground level to rooftop or solar plant area with sufficient water Extra pressure to clean the solar modules.
Note on A274: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Water flow meters are essential devices for measuring the amount of water flowing through pipelines to measure the amount of water we are utilized in particular plant.
Note on A275: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Pressure relief valves (PRVs) are crucial safety devices in water pipelines and systems, particularly those using UPVC/CPVC pipes. They are designed to automatically open and release excess pressure when it exceeds a predetermined safe limit, protecting the system from potential damage and ensuring operational safety.
Note on A276: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Copper ring lugs are indispensable components for ensuring the safe and reliable earthing of solar panel module frames. In a solar installation, proper grounding of the module frames is critical to prevent electric shock hazards and protect the entire system from potential damage due to lightning strikes or electrical faults
Note on A277: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Copper ring lugs are indispensable components for ensuring the safe and reliable earthing of solar panel module frames. In a solar installation, proper grounding of the module frames is critical to prevent electric shock hazards and protect the entire system from potential damage due to lightning strikes or electrical faults
Note on A278: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Bimetallic lugs are specialized electrical connectors used to create a secure and electrically sound connection between two conductors made of different metals, typically aluminum and copper
Note on A279: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Bimetallic lugs are specialized electrical connectors used to create a secure and electrically sound connection between two conductors made of different metals, typically aluminum and copper
Note on A280: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Bimetallic lugs are specialized electrical connectors used to create a secure and electrically sound connection between two conductors made of different metals, typically aluminum and copper
Note on A281: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Bimetallic lugs are specialized electrical connectors used to create a secure and electrically sound connection between two conductors made of different metals, typically aluminum and copper
Note on A282: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Bimetallic lugs are specialized electrical connectors used to create a secure and electrically sound connection between two conductors made of different metals, typically aluminum and copper
Note on A283: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Bimetallic lugs are specialized electrical connectors used to create a secure and electrically sound connection between two conductors made of different metals, typically aluminum and copper
Note on A284: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Bimetallic lugs are specialized electrical connectors used to create a secure and electrically sound connection between two conductors made of different metals, typically aluminum and copper
Note on A285: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Bimetallic lugs are specialized electrical connectors used to create a secure and electrically sound connection between two conductors made of different metals, typically aluminum and copper
Note on A286: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Bimetallic lugs are specialized electrical connectors used to create a secure and electrically sound connection between two conductors made of different metals, typically aluminum and copper
Note on A287: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Bimetallic lugs are specialized electrical connectors used to create a secure and electrically sound connection between two conductors made of different metals, typically aluminum and copper
Note on A288: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Bimetallic lugs are specialized electrical connectors used to create a secure and electrically sound connection between two conductors made of different metals, typically aluminum and copper
Note on A290: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Bimetallic lugs are specialized electrical connectors used to create a secure and electrically sound connection between two conductors made of different metals, typically aluminum and copper
Note on A291: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Bimetallic lugs are specialized electrical connectors used to create a secure and electrically sound connection between two conductors made of different metals, typically aluminum and copper
Note on A293: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Aluminum lugs are electrical connectors specifically designed to terminate and connect aluminum conductors to various electrical devices, equipment, or other conductors
Note on A294: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Aluminum lugs are electrical connectors specifically designed to terminate and connect aluminum conductors to various electrical devices, equipment, or other conductors
Note on A295: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Aluminum lugs are electrical connectors specifically designed to terminate and connect aluminum conductors to various electrical devices, equipment, or other conductors
Note on A296: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Aluminum lugs are electrical connectors specifically designed to terminate and connect aluminum conductors to various electrical devices, equipment, or other conductors
Note on A297: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Aluminum lugs are electrical connectors specifically designed to terminate and connect aluminum conductors to various electrical devices, equipment, or other conductors
Note on A298: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Aluminum lugs are electrical connectors specifically designed to terminate and connect aluminum conductors to various electrical devices, equipment, or other conductors
Note on A299: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Aluminum lugs are electrical connectors specifically designed to terminate and connect aluminum conductors to various electrical devices, equipment, or other conductors
Note on A300: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Aluminum lugs are electrical connectors specifically designed to terminate and connect aluminum conductors to various electrical devices, equipment, or other conductors
Note on A301: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Aluminum lugs are electrical connectors specifically designed to terminate and connect aluminum conductors to various electrical devices, equipment, or other conductors
Note on A302: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Aluminum lugs are electrical connectors specifically designed to terminate and connect aluminum conductors to various electrical devices, equipment, or other conductors
Note on A303: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Aluminum lugs are electrical connectors specifically designed to terminate and connect aluminum conductors to various electrical devices, equipment, or other conductors
Note on A304: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: BOS material Loading and transport through the road and it will reach to the site. All type of approvals and permission included
Note on A307: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Maintaining a well-stocked spare parts inventory is crucial for ensuring the reliability, efficiency, and continuous operation of a solar power plant.
Note on A308: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Total plant insurance, often referred to as specialized renewable energy insurance, is a critical component for safeguarding solar power plants against a wide range of risks. It provides comprehensive coverage for the entire facility, including both the solar modules and the Balance of System (BOS) components (inverters, structures, cabling, substation, etc. )
Note on A311: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Thermography uses infrared cameras to detect "hot spots" (excess heat) in electrical systems, identifying issues like loose connections or insulation failure for predictive maintenance, while a Power Analyzer precisely measures electrical parameters (voltage, current, power, harmonics) to quantify energy use, quality, and efficiency
Note on A312: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Galvanized Iron (GI) conduits are essential for protecting electrical cables in solar power plants, offering durability against harsh environmental conditions
Note on A313: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Kind of Bank grandee
Note on A314: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Module frame earthing, also known as array earthing or grounding, is a critical safety and performance measure in solar PV systems. It involves securely connecting the metallic frames of the solar panels and their mounting structures to the overall earthing system of the solar installation.
Note on A315: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: ETAP Load Flow Analysis is a power system simulation using ETAP software to analyze the steady-state performance of electrical networks, calculating bus voltages, line loadings, power flows, and losses to identify issues like voltage violations or overloaded equipment, crucial for system planning and operation.
Note on A316: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To display the current value of plant performance.
Note on A319: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This having 1.5 mtrs height ladder used to clean the RCC mounted installation modules
Note on A320: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Movable ladders in parking structures serve various crucial purposes, mainly focusing on maintenance, accessibility, and safety within these often large and complex environments.
Note on A321: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Structural Stability (Mechanical): Focuses on the mounting system and building integration, checking against wind loads, snow, and seismic events.
Note on A333: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: In the context of solar installations, project management is crucial for successfully installing and commissioning solar power plants, whether on rooftops or as large-scale solar farms
Note on A334: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: A Safety Officer, also known as an EHS (Environmental, Health, and Safety) Officer, plays a critical and multifaceted role in ensuring safety, regulatory compliance, and a secure working environment throughout the entire lifecycle
Note on A335: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Setting up a solar shed on a rooftop involves a combination of civil engineering and the installation and commissioning (I&C) of the solar power system. This process ensures the structure is sound, the solar panels are securely mounted, and the electrical system is properly connected and functioning.
Note on A336: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Setting up a solar RCC on a rooftop involves a combination of civil engineering and the installation and commissioning (I&C) of the solar power system. This process ensures the structure is sound, the solar panels are securely mounted, and the electrical system is properly connected and functioning.
Note on A337: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Setting up a solar RCC raised (2.5mtrs) on a rooftop involves a combination of civil engineering and the installation and commissioning (I&C) of the solar power system. This process ensures the structure is sound, the solar panels are securely mounted, and the electrical system is properly connected and functioning.
Note on A338: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Setting up a solar RCC raised (2.5mtrs) on a rooftop involves a combination of civil engineering and the installation and commissioning (I&C) of the solar power system. This process ensures the structure is sound, the solar panels are securely mounted, and the electrical system is properly connected and functioning.
Note on A339: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Setting up a solar RCC raised on the exiting pillar (2.5mtrs) on a rooftop involves a combination of civil engineering and the installation and commissioning (I&C) of the solar power system. This process ensures the structure is sound, the solar panels are securely mounted, and the electrical system is properly connected and functioning.
Note on A340: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Setting up a solar Ground involves a combination of civil engineering and the installation and commissioning (I&C) of the solar power system. This process ensures the structure is sound, the solar panels are securely mounted, and the electrical system is properly connected and functioning.
Note on A341: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Setting up a solar Ground raised 3 mtrs height involves a combination of civil engineering and the installation and commissioning (I&C) of the solar power system. This process ensures the structure is sound, the solar panels are securely mounted, and the electrical system is properly connected and functioning.
Note on A342: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Setting up a solar Ground raised 6 mtrs height involves a combination of civil engineering and the installation and commissioning (I&C) of the solar power system. This process ensures the structure is sound, the solar panels are securely mounted, and the electrical system is properly connected and functioning.
Note on A343: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Setting up a solar Floating involves a combination of civil engineering and the installation and commissioning (I&C) of the solar power system. This process ensures the structure is sound, the solar panels are securely mounted, and the electrical system is properly connected and functioning.
Note on A344: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Providing a dedicated stand with a protective canopy for the inverter is a critical step in ensuring the longevity, performance, and safety of a solar power system
Note on A345: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Providing a dedicated stand with a protective canopy for the inverter is a critical step in ensuring the longevity, performance, and safety of a solar power system
Note on A346: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Soil trenching for electrical cables is a process that involves digging a trench in the ground to lay electrical cables. This method provides physical protection for the cables and helps to maintain a consistent temperature, which is important for the performance and lifespan of the cables
Note on A348: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This involves digging a trench across the road, laying the cable within the trench, and then backfilling.
Note on A349: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: A cable gantry is a structure that supports and organizes electrical cables, particularly in areas where overhead routing is necessary or preferable to underground trenching. While the term "gantry" is most commonly associated with gantry cranes used for heavy lifting, it also refers to structures that support cables, especially in industrial Rooftops
Note on A351: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Accurate knowledge of soil properties like bearing capacity, cohesion, and compressibility is crucial for designing a strong and stable foundation that can support the panel and associated infrastructure without excessive settlement, cracks, or potential collapse.
Note on A352: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Reshaping the land to achieve a flat or uniformly sloped surface suitable for solar panel installation and the associated infrastructure.
Note on A353: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: A bathymetry test (or survey) measures the depth and shape of the underwater terrain (seafloor, lakebeds) using technologies like sonar (multibeam echo sounders) and Lidar, creating detailed maps for navigation, engineering, and environmental studies, analogous to topography for land. These surveys help create nautical charts, map underwater features, study water quality, and assess risks like scour, involving precise positioning and data processing to understand underwater landscapes.
Note on A354: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: CFD analysis (Computational Fluid Dynamics) uses numerical methods and computer simulations to study and predict how liquids and gases (fluids) flow and interact with objects or systems
Note on A355: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To approach the Plant from exiting road
Note on A356: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Providing access for routine maintenance tasks like cleaning, inspections, and repairs of the solar panels and associated equipment.
Note on A357: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Peripheral roads facilitate security patrols and surveillance activities, helping prevent theft and vandalism. Regular patrols along these roads allow for quicker detection of unauthorized entry or suspicious activities.
Note on A358: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Stormwater drainage systems are essential infrastructure designed to manage excess rainwater and melted snow from various surfaces, primarily impervious one solar plant area ground mounted locations.
Note on A359: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Many inverter control rooms are prefabricated, built using lightweight and insulated sandwich panels to keep the other electronics device like battery LT panel etc.
Note on A365: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: CEIG liaisoning cost covers expenses related to obtaining approvals, inspections, and certifications from the Chief Electrical Inspector to Government for electrical installations.
Note on A366: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: NOC (No Objection Certificate) from DISCOMs is a crucial requirement for setting up solar power plants in India. This certificate ensures that your solar system complies with the DISCOM's grid connection and safety standards. Without an NOC, you cannot proceed with your solar installation.
Note on A367: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Net metering is a crucial mechanism that allows owners of solar PV systems to send surplus electricity generated back to the grid and receive credits for it, effectively reducing their overall electricity bills. In India, this process often involves the use of ABT (Availability Based Tariff) meters, particularly for larger installations or high-tension consumers
Note on A368: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: In India, installing a solar power plant, especially an on-grid or net-metered system, involves a variety of statutory fees and charges levied by different government bodies and agencies. These fees can vary significantly based on factors such as the size and type of the plant (e.g., residential rooftop vs. utility-scale), the specific state, and the local electricity distribution company (DISCOM).
Note on A369: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Metering cubicles are vital for businesses and infrastructure projects that rely on efficient and accurate energy management. They are used in applications like substations, industrial plants, and utility installations to monitor and record electricity usage for billing, monitoring, and optimization
Note on A371: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Applicable for Tamil nadu state
Note on A372: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Applicable for Tamil nadu state
Note on A373: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: It measures the amount of electricity generated by the solar system (in kWh) and how much of it is sent to your load (and possibly to the grid).
Note on A375: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The Renewable Purchase Obligation (RPO) is a critical regulatory mechanism in India designed to promote the generation and consumption of electricity from renewable energy (RE) sources. Mandated by the Electricity Act, 2003, and subsequently elaborated upon by the Central and State Electricity Regulatory Commissions (CERC/SERCs), the RPO framework requires certain obligated entities to procure a specified percentage of their electricity from RE sources
Note on A376: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Applicable only on MP state
Note on A377: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Running cost for MP State
Note on A378: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: the solar capacity in AP exceeds 1 MW, you must go through a special approval process, and you’ll incur higher application charges MW as per the draft APERC regulations
Note on A379: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The seamless communication between Remote Terminal Units (RTUs) at solar power plants and the State Load Despatch Centres (SLDCs) is critical for efficient grid integration, monitoring, and control of renewable energy (RE) generation. This communication ensures grid stability, optimizes power flow, and helps manage the intermittent nature of solar power.## I. Importance of communication
Note on A380: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: In India, the term "DISCOM meter" refers to the electricity meter provided and managed by the local Distribution Company (DISCOM). This meter plays a crucial role in the financial accounting and operation of solar power plants, particularly those connected to the grid. There are two primary types of metering arrangements employed by DISCOMs for solar rooftop plants: net metering and gross metering.
Note on A386: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: EPC Margin represents the profit margin added by the Engineering, Procurement, and Construction contractor for managing and executing the complete project scope efficiently and successfully.
Note on A387: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Marketing commission is the fee paid to agents or agencies for promoting and securing project orders, contributing to business growth and client acquisition.
Note on A391: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Annual Maintenance Contract (AMC) covers scheduled servicing, repairs, and technical support to ensure reliable operation and longevity of equipment throughout the year.
Note on A392: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Applicable for ITC Projects
Note on A395: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Solar CAPEX (Capital Expenditure) costs refer to the upfront investment required to purchase, install, and commission a solar energy system. Essentially, it's the initial capital outlay a business or individual makes to own the solar power plant outright.
Note on A397: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: A BG is a financial instrument issued by a bank that ensures the fulfillment of contractual or financial obligations. If a party fails to meet their obligations, the bank will step in and cover the losses up to the guaranteed amount.
Note on A399: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Capex cost including BG Value
Note on A401: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: In India, the Goods and Services Tax (GST) applies to solar power projects, though with specific rates and regulations designed to balance tax revenue with the promotion of renewable energy.
Note on A403: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: OPEX or Operating Expenditure refers to the ongoing costs incurred to run and maintain a solar power plant throughout its operational lifetime.
Note on A591: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Optimizers utilize Maximum Power Point Tracking (MPPT) technology at the individual panel level. This means they constantly monitor the voltage and current of each panel, adjusting its electrical characteristics to ensure it operates at its peak power output, regardless of the performance of other panels in the array.

## Sheet4
238
|  | 400 | 638
MPPT - 1 | Str - 1 | 18
| Str - 2 | 18
MPPT - 2 | Str - 3 | 18
| Str - 4 | 18
MPPT - 3 | Str - 5 | 18
| Str - 6 | 18
MPPT - 4 | Str - 7 | 18
Str - 8
MPPT - 5 | Str - 9
| Str - 10 | 19
MPPT - 6 | Str - 11 | 19
Str - 12
MPPT - 7 | Str - 13 | 19
| Str - 14 | 19
MPPT - 8 | Str - 15
| Str - 16 | 19
MPPT - 9 | Str - 17 | 19
Str - 18
MPPT - 10 | Str - 19 | 19
| Str - 20 | 19
125

## Sheet3 (hidden)
Items | Units | Makes | Items | Units | Makes
Floating Structure Along with cable Trays | kWp | Reputed make | M4x20mm for module frame earthing | No's
Hardware for RCC/RCC Raised/ Ground mounted/ Parking | Tons | Reputed make | M8x15mm for walkways | No's
Railings on Roof Edge's with toe guard | Mtr's |  | Hose pipe for water | Mtr's
Mesh Over the Skylight width <600mm | Rmtr's | GI | 25 mm CPVC Pipe for Water piping & array looping purpose | Mtr's | Birla/ Equilent
Mesh Over the Skylight width 600-1200mm | Rmtr's |  | 25 mm CPVC T-bend | No's
Mesh Over the Skylight width 1200-1700mm | Rmtr's |  | 25 mm CPVC L-bend | No's
Mesh Over the Skylight width 1700-2200mm | Rmtr's |  | 25 mm CPVC Ball value | No's
Gutter length for Cleaning / Rain water harvesting | Mtr's | Reputed make | 25 mm CPVC Coupler | No's
Gutters Dropdown for every 10 mtrs length | No's | Reputed make | CVPC Solution 934ml | No's
Module Temperature Sensor | No's | Any Reputed Make | CPVC Pipe C Clamp | No's
Ambient Temperature Sensor | No's |  | CPVC Pipe End cap | No's
Anemometer | No's |  | 25mm CPVC MTA and FTA | No's
Rain gauge Sensor | No's |  | 25mm CPVC Union | No's
Weather Station Tripod Mounting Stand with junction box | No's |  | 600 KVA UPS | No's
Data Logger | No's |  | Earthing name plates | No's
Humidity Sensor | No's |  | Danger board AC 415V and DC 1500V | No's
Earth Strip Clamps | No's | Reputed make | Fourthpartner Name Plant | No's
M8X25 Self triding screw and wooden Gutties | No's | Reputed make | LT Cable Route marker | No's
M8x25mm for Earth Strip and cable tray | No's | Reputed make | Insulation mats 1Mtrx1Mtr for Inverter & ACCB 3.3kv | No's
Base clamp 100mm | No's | Reputed make | Hume Pipe 300mm Dia | Mtr's
M-clamp SS - Walkway clamps | No's | Reputed make | DWC Pipe for Ground Mounted Type | Mtr's | Nagarjuna polymers / Equilent
M8x15mm Walkway jointer with hardware | No's | Reputed make | DWC Pipe T bend | No's
Step and Zero degree walkway Supports GI raised Leg | No's | Reputed make | DWC Pipe L bend | No's
Bus Insulators for LA strip | No's | Reputed make | DWC Pipe Coupler | No's
32mm Flexible Pipe used for module to cable Tray | Mtr's | Reputed make | PVC Water Tank 5000 Ltrs | No's | Sintex/ Equilent
Industrial wall socket box with MCB (Single phase two pole) | No's |  | PVC Water Tank 2000 Ltrs | No's
Industrial wall socket box with MCB (Three phase four pole) | No's |  | 1 HP Water pump | No's | Crompton Greaves/ Equilent
Module water drainage clips | No's |  | 1.5 HP Water pump | No's
Cable Ties -Nylon 150mm | Packet's |  | Booster Water pump | No's
Cable Ties -Nylon 200mm | Packet's |  | Water flow meter | No's
Cable Ties -Nylon 300mm | Packet's |  | Water Pressure release Value | No's
Cable Ties -Nylon 450mm | Packet's |  | 2.5 Sqmm Cu. & Bimetallic Lug's Pin & Ring type | No's | Dowell's/ Equilent
Cable Ties -SS 200mm | Packet's |  | 4 Sqmm Cu. Lug's Round type | No's
Cable Ties -SS 300mm | Packet's |  | 16 Sqmm Cu. & Bimetallic Lug's Pin & Ring type | No's
Cable Ties -SS 500mm | Packet's |  | 25 Sqmm Cu. & Bimetallic Lug's Pin & Ring type | No's
LA support- 3 mtrs GI pipe | No's |  | 35 Sqmm Cu. & Bimetallic Lug's Pin & Ring type | No's
Stay wires for LA | Mtr's |  | 50 Sqmm Cu. & Bimetallic Lug's Pin & Ring type | No's
MC4 connector Male and Female | No's |  | 70 Sqmm Cu. & Bimetallic Lug's Pin & Ring type | No's
Inlie Fuse Male & Female | No's | Elmax/ Equilent | 16 Sqmm Bimetallic Lug's Pin type | No's
DC cable dressing clips | No's |  | 25 Sqmm Bimetallic Lug's Pin type | No's
Fire extinguisher CO2 | No's |  | 35 Sqmm Bimetallic Lug's Pin type | No's
Fire Bucket with Stand and canopy | No's |  | 50 Sqmm Bimetallic Lug's Pin type | No's
Fire extinguisher ABC type | No's |  | 70 Sqmm Bimetallic Lug's Pin type | No's
Conduit pipe fixing(joining) Solvent (1000 ml) | No's |  | 95 Sqmm Bimetallic Lug's Pin type | No's
Pu sealant for closing the opening of the pipes/conduits | No's |  | 185 Sqmm Bimetallic Lug's Pin type | No's
Sleeves each colour 250mm length Inv. To ACCB panel | Mtr's |  | 240 Sqmm Bimetallic Lug's Pin type | No's
Sleeves each colour 250mm ACCB panel to Termination | Mtr's |  | 16 Sqmm AL. Lug's Ring type | No's
PVC Tape (R, Y, B, B, G) | No's |  | 25 Sqmm AL. Lug's Ring type | No's
Ferrules | No's |  | 35 Sqmm AL. Lug's Ring type | No's
150 Sqmm AL. Lug's Ring type | No's | Dowell's/ Equilent | 50 Sqmm AL. Lug's Ring type | No's
185 Sqmm AL. Lug's Ring type | No's |  | 70 Sqmm AL. Lug's Ring type | No's
240 Sqmm AL. Lug's Ring type | No's |  | 95 Sqmm AL. Lug's Ring type | No's
300 Sqmm AL. Lug's Ring type | No's |  | 120 Sqmm AL. Lug's Ring type | No's
Freight & Handling By Road | Truck | Goods Transportation (Only BOS)

## Sheet2 (hidden)
0
| 0.5 HP | 2850
| 1 HP | 3850 |  | g488 | Base 24 mm -ECO 70
| 1.5 HP | 10200 |  | g489 | Trapezoidal or curve type
| 2 HP | 14500 |  | g490 | Land scape - 300MM
| booster | 24000 | 400 | g491 | Land scape - 250MM
|  |  | 40 | g492 | Base 40 mm - SSP 1032
#N/A

## Item's Make (hidden)
Sr.no. | Item's | 4PEL Standard Make's
1 | Inverter | Solis
2 | MMS for Shed | SMS, EPDM gasket (bimettalic)
| MMS for RCC & Ground | Fourth Partner Energy- MS Hot dip galvanization (min. 80 micron thickness) with 180kmph (Steel-TATA, JSW,Jindal)(Tubes -Appolo)
4 | LT Panel | Indus, Bhagyashree, Accupanels, Sanjay tec, LS power
5 | Switch Gears | Schneider, L&T, ABB
6 | Chemical Earthing | Indelec/ LPI
7 | DC Cu. Cable | Polycab
8 | Branch Connectors (Inland fuse) | Elmax
9 | AC Cable | Polycab
10 | Lightening Arrestor | LPI
11 | Water Pipe | Astral
12 | Harizonal Walkways | MOC/FRP
13 | Cable Tray | GI/FRP
14 | DWC Pipe | Nagarjuna polymers/dura.line
15 | Lifeline | Joykco/Life Gear
16 | Remote monitoring system | Wattmon
17 | Irradiation sensor | Ingenieurburo
18 | Pyranometer | Kripp Zonen
19 | Zero Feeding device | Wattmon
20 | DG Protection device | Wattmon
21 | Generation Panel before client | Indus, Bhagyashree, Accupanels, Sanjay tec, LS power
22 | Net metering Materials | Secure / L&T
23 | Metering Cubicle (CT&PT) | Kalpa/Kappa
-19533
|  |  | 2381600 | 31600 | 4.58
|  |  | 110000 | 2350000
| 374446 |  | 2491600
| 223154 | 223154 | 47632
| 151292 | 0.60743 | 2539232
|  | 1207086 | 277208.7336 |  | 1700000
|  | 976846 |  |  | 839232 | 800000
| 40.4% | 230240 | 2600000
|  | 1574460 | 60768 |  | 1581232
|  | 367374 |  |  | 158123.2
89800
|  | 14 | 113000
|  | 367374 | 23200
82820
2600000
-2517180
|  |  | 958000 | 479000 |  | 104585.1528
|  | stamp | 67060 | 33530 | 33530
|  | reg. fees | 19160 | 9580
|  | other | 3000 | 3000
|  | office exp. | 3000 | 3000
|  | fees | 8000 | 8000
|  |  | 100220 | 57110
114220

## Sheet1 (hidden)
Sl no. | Name of the Item's | Current price | Updated Price | Price Diviation
1 | 1CX4 Sqmm DC solar cable 1.8kV XLPO, FRLS | 43 | 44 | -1 |  |  | 13050
2 | 1CX6 Sqmm DC solar cable 1.8kV XLPO, FRLS | 62 | 63 | -1 |  |  | 10000
3 | 4CX16Sqmm Cu XLPE AC Copper Un- Armoured Cable-1.1kV | 1044 |  | 1044 |  |  | 6500
4 | 4CX25Sqmm Cu XLPE AC Copper Un- Armoured Cable-1.1kV | 1737 |  | 1737 |  |  | 5000
5 | 4CX16Sqmm Al XLPE AC Aluminium Armoured Cable-1.1kV | 117.9 |  | 117.9
6 | 3.5CX25Sqmm Al XLPE AC Aluminium Armoured Cable -1.1kV | 165.6 |  | 165.6
7 | 3.5CX35Sqmm Al XLPE AC Aluminium Armoured Cable-1.1kV | 187.2 |  | 187.2
8 | 3.5CX50Sqmm Al XLPE AC Aluminium Armoured Cable -1.1kV | 253.5 |  | 253.5
9 | 3.5CX70Sqmm Al XLPE AC Aluminium Armoured Cable -1.1kV | 346.5 |  | 346.5
10 | 3.5CX95Sqmm Al XLPE AC Aluminium Armoured Cable -1.1kV | 441 |  | 441 |  | total | 2381600
11 | 3.5CX120Sqmm Al XLPE AC Aluminium Armoured Cable-1.1kV | 567 |  | 567 |  | DD | 958000
12 | 3.5CX150Sqmm Al XLPE AC Aluminium Armoured Cable -1.1kV | 663.3 |  | 663.3 |  | cash | 1423600
13 | 3.5CX185Sqmm Al XLPE AC Aluminium Armoured Cable -1.1kV | 848.4 |  | 848.4 |  |  | 1480000
14 | 3.5CX240Sqmm Al XLPE AC Aluminium Armoured Cable-1.1kV | 1038.3 |  | 1038.3 |  |  | 56400
15 | 3.5CX300Sqmm Al XLPE AC Aluminium Armoured Cable -1.1kV | 1345.5 |  | 1345.5 |  | docu. | 110000
16 |  |  |  | 0 |  | SC | 47632
157632
101232
[5 empty] | 716700 | 37188 | 44288
|  |  |  | 753888 | 742693 | -11195 | -18295
| 2500000 | 3253860 | 753860 |  | 1207086
1 | 54231 | 3199629 | 2025-08-07 | 26241 | 1180845 |  | 80472
2 | 54231 | 3145398 | 2025-08-08 | 26241 | 1154604 |  | 80472
3 | 54231 | 3091167 | 2025-08-09 | 26241 | 1128363 |  | 80472
4 | 54231 | 3036936 | 2025-08-10 | 26241 | 1102122 |  | 80472
5 | 54231 | 2982705 | 2025-08-11 | 26241 | 1075881 |  | 80472
6 | 54231 | 2928474 | 2025-08-12 | 26241 | 1049640 |  | 80472
7 | 54231 | 2874243 | 2026-08-01 | 26241 | 1023399 |  | 80472
8 | 54231 | 2820012 | 2026-08-02 | 26241 | 997158 |  | 80472
9 | 54231 | 2765781 | 2026-08-03 | 26241 | 970917 |  | 80472
10 | 54231 | 2711550 | 2026-08-04 | 26241 | 944676 |  | 80472
11 | 54231 | 2657319 | 2026-08-05 | 26241 | 918435 |  | 80472
12 | 54231 | 2603088 | 2026-08-06 | 26241 | 892194 |  | 80472
13 | 54231 | 2548857 | 2026-08-07 | 26241 | 865953 |  | 80472
14 | 54231 | 2494626 | 2026-08-08 | 26241 | 839712 |  | 80472
15 | 54231 | 2440395 | 2026-08-09 | 26241 | 813471 |  | 80472
16 | 54231 | 2386164 | 2026-08-10 | 26241 | 787230 |  | 80472
17 | 54231 | 2331933 | 2026-08-11 | 26241 | 760989 |  | 80472
18 | 54231 | 2277702 | 2026-08-12 | 26241 | 734748 |  | 80472
19 | 54231 | 2223471 | 2027-08-01 | 26241 | 708507 |  | 80472
20 | 54231 | 2169240 | 2027-08-02 | 26241 | 682266 |  | 80472
21 | 54231 | 2115009 | 2027-08-03 | 26241 | 656025 |  | 80472
22 | 54231 | 2060778 | 2027-08-04 | 26241 | 629784 |  | 80472
23 | 54231 | 2006547 | 2027-08-05 | 26241 | 603543 |  | 80472
24 | 54231 | 1952316 | 2027-08-06 | 26241 | 577302 |  | 80472
25 | 54231 | 1898085 | 2027-08-07 | 26241 | 551061 |  | 80472
26 | 54231 | 1843854 | 2027-08-08 | 26241 | 524820 |  | 80472
27 | 54231 | 1789623 | 2027-08-09 | 26241 | 498579 |  | 80472
28 | 54231 | 1735392 | 2027-08-10 | 26241 | 472338 |  | 80472
29 | 54231 | 1681161 | 2027-08-11 | 26241 | 446097 |  | 80472
30 | 54231 | 1626930 | 2027-08-12 | 26241 | 419856 |  | 80472
31 | 54231 | 1572699 | 2028-08-01 | 26241 | 393615 |  | 80472
32 | 54231 | 1518468 | 2028-08-02 | 26241 | 367374 |  | 80472
33 | 54231 | 1464237 | 2028-08-03 | 26241 | 341133 |  | 80472
34 | 54231 | 1410006 | 2028-08-04 | 26241 | 314892 |  | 80472
35 | 54231 | 1355775 | 2028-08-05 | 26241 | 288651 |  | 80472
36 | 54231 | 1301544 | 2028-08-06 | 26241 | 262410 |  | 80472
37 | 54231 | 1247313 | 2028-08-07 | 26241 | 236169 |  | 80472
38 | 54231 | 1193082 | 2028-08-08 | 26241 | 209928 |  | 80472
39 | 54231 | 1138851 | 2028-08-09 | 26241 | 183687 |  | 80472
40 | 54231 | 1084620 | 2028-08-10 | 26241 | 157446 |  | 80472
41 | 54231 | 1030389 | 2028-08-11 | 26241 | 131205 |  | 80472
42 | 54231 | 976158 | 2028-08-12 | 26241 | 104964 |  | 80472
43 | 54231 | 921927 | 2029-08-01 | 26241 | 78723 |  | 80472
44 | 54231 | 867696 | 2029-08-02 | 26241 | 52482 |  | 80472
45 | 54231 | 813465 | 2029-08-03 | 26241 | 26241 |  | 80472
46 | 54231 | 759234 | 2029-08-04 | 26241 | 0 |  | 80472
47 | 54231 | 705003 | 2029-08-05 |  |  |  | 54231
48 | 54231 | 650772 | 2029-08-06 |  |  |  | 54231
49 | 54231 | 596541 | 2029-08-07 |  |  |  | 54231
50 | 54231 | 542310 | 2029-08-08 |  |  |  | 54231
51 | 54231 | 488079 | 2029-08-09 |  |  |  | 54231
52 | 54231 | 433848 | 2029-08-10 |  |  |  | 54231
53 | 54231 | 379617 | 2029-08-11 |  |  |  | 54231
54 | 54231 | 325386 | 2029-08-12 |  |  |  | 54231
55 | 54231 | 271155 | 2030-08-01 |  |  |  | 54231
56 | 54231 | 216924 | 2030-08-02 |  |  |  | 54231
57 | 54231 | 162693 | 2030-08-03 |  |  |  | 54231
58 | 54231 | 108462 | 2030-08-04 |  |  |  | 54231
59 | 54231 | 54231 | 2030-08-05 |  |  |  | 54231
60 | 54231 | 0 | 2030-08-06 |  |  |  | 54231
| 3253860 |  |  | 1207086 |  |  | 4460946